## Bore Pump MMII
Equipment | Item Name | Tag Type | Set Trend | Category | Tag Name | Cluster Name | I/O Device | Data Type | Address | Comment | Deadband | Eng Units | Format | Raw Zero Scale | Raw Full Scale | Eng Zero Scale | Eng Full Scale | Custom 1 | Custom 2 | Custom 3 | Custom 4 | Custom 5 | Custom 6 | Custom 7 | Custom 8 | Historize | Project | EDITCODE | LINKED | OID | REF1 | REF2 | CUSTOM | TAGGENLINK
[5 empty] | Alarm |  |  |  | 10384
[5 empty] | Analog |  |  |  | 3911
[5 empty] | Status |  |  |  | 1384
[5 empty] | Totalisers |  |  |  | 10240
SFC_BP13 |  | Status |  |  | S_SFC_BP13_CLDWN |  |  | DIGITAL | %M1384 | Cooling Down
|  | Status |  |  | S_SFC_BP13_AUTO |  |  | DIGITAL | %M1385 | Auto
|  | Status |  |  | S_SFC_BP13_MAN |  |  | DIGITAL | %M1386 | Manual
|  | Status |  |  | S_SFC_BP13_LOCAL |  |  | DIGITAL | %M1387 | Local
|  | Status |  |  | S_SFC_BP13_OTM |  |  | DIGITAL | %M1388 | Out to Maintenance
|  | Status |  |  | S_SFC_BP13_OFF |  |  | DIGITAL | %M1389 | Off
|  | Status |  |  | S_SFC_BP13_RDY |  |  | DIGITAL | %M1390 | Ready
|  | Status |  |  | S_SFC_BP13_RUNNG |  |  | DIGITAL | %M1391 | Running
|  | Status |  |  | S_SFC_BP13_BIT1 |  |  | DIGITAL | %M1392 | Status Bit 1
|  | Status |  |  | S_SFC_BP13_BIT2 |  |  | DIGITAL | %M1393 | Status Bit 2
|  | Status |  |  | S_SFC_BP13_BIT3 |  |  | DIGITAL | %M1394 | Status Bit 3
|  | Status |  |  | S_SFC_BP13_BIT4 |  |  | DIGITAL | %M1395 | Status Bit 4
|  | Status |  |  | S_SFC_BP13MOTOR_HLTY |  |  | DIGITAL | %M1396 | Motor Healthy
|  | Status |  |  | S_SFC_BP13LOS_HLTY |  |  | DIGITAL | %M1397 | Emergency Stop Healthy
|  | Status |  |  | S_SFC_BP13_REMRDY |  |  | DIGITAL | %M1398 | Remote Ready
|  | Status |  |  | S_SFC_BP13POWER_ON |  |  | DIGITAL | %M1399 | Mains Power On
|  | Status |  |  | S_SFC_BP13_COMMSINHIBIT |  |  | DIGITAL | %M1400 | Communication Inhibited
|  | Alarm |  | TP_CRIT_CAT | A_SFC_BP13FT01_LO |  |  | DIGITAL | %M10384 | Low Flow
|  | Alarm |  | TP_CRIT_CAT | A_SFC_BP13CA1_FTO |  |  | DIGITAL | %M10385 | Contactor Failed to Open
|  | Alarm |  | TP_CRIT_CAT | A_SFC_BP13CA1_FTC |  |  | DIGITAL | %M10386 | Contactor Failed to Close
|  | Alarm |  | TP_CRIT_CAT | A_SFC_BP13MOTOR_FLT |  |  | DIGITAL | %M10387 | Motor Fault
|  | Alarm |  | TP_CRIT_CAT | A_SFC_BP13LOS_FLT |  |  | DIGITAL | %M10388 | Emergency Stop Fault
|  | Alarm |  | TP_CRIT_CAT | A_SFC_BP13POWER_FAIL |  |  | DIGITAL | %M10389 | Mains Power Fault
|  | Alarm |  | TP_CRIT_CAT | A_SFC_BP13_R0S1_FLT |  |  | DIGITAL | %M10390 | PLC Rack 0 Slot 1 Fault
|  | Alarm |  | TP_CRIT_CAT | A_SFC_BP13_R0S2_FLT |  |  | DIGITAL | %M10391 | PLC Rack 0 Slot 2 Fault
|  | Alarm |  | TP_CRIT_CAT | A_SFC_BP13FT01_BPV |  |  | DIGITAL | %M10392 | Flow Transmitter Error
|  | Alarm |  | TP_CRIT_CAT | A_SFC_BP13IT01_BPV |  |  | DIGITAL | %M10393 | Current Transmitter Error
|  | Alarm |  | TP_CRIT_CAT | A_SFC_BP13LT01_BPV |  |  | DIGITAL | %M10394 | Level Transmitter Error
|  | Alarm |  | TP_CRIT_CAT | A_SFC_BP13PT01_BPV |  |  | DIGITAL | %M10395 | Pressure Transmitter Error
|  | Alarm |  | TP_CRIT_CAT | A_SFC_BP13_ETH_RST |  |  | DIGITAL | %M10396 | PLC Ethernet Port Successfully Reset
|  | Alarm |  | TP_CRIT_CAT | A_SFC_BP13_PROJ |  |  | DIGITAL | %M10397 | PLC Project has Changed
|  | Alarm |  | TP_CRIT_CAT | A_SFC_BP13_FORCES |  |  | DIGITAL | %M10398 | PLC Number of Forces has Changed
|  | Alarm |  | TP_COMMS_CAT | A_SFC_BP13_COMMS |  |  | DIGITAL | %M10399 | Comms HB Timeout
|  | Alarm |  | TP_CRIT_CAT | A_SFC_BP13P110_Fail |  |  | DIGITAL | %M10400 | 110V Fault
|  | Alarm |  | TP_CRIT_CAT | A_SFC_BP13DECON_FLT |  |  | DIGITAL | %M10401 | Decontactor Fault
|  | Alarm |  | TP_CRIT_CAT | A_SFC_BP13LA_FLT |  |  | DIGITAL | %M10402 | Lighting Arrestor Fault
|  | Alarm |  | TP_CRIT_CAT | A_SFC_BP13SS_FLT |  |  | DIGITAL | %M10403 | Soft Starter Fault
|  | Alarm |  | TP_CRIT_CAT | A_SFC_BP13CA1_CLSD |  |  | DIGITAL | %M10404 | Main Contactor Not Closed
|  | Alarm |  | TP_CRIT_CAT | A_SFC_BP13CA2_CLSD |  |  | DIGITAL | %M10405 | Bypass Contactor Not Closed
|  | Alarm |  | TP_COMMS_CAT | A_SFC_BP13MMII_COMMS |  |  | DIGITAL | %M10406 | MMII Comms Fault
|  | Analog | TRUE |  | N_SFC_BP13FT01_PV |  |  | INT | %MW3911 | Discharge Flow |  | m³/Hr | ###EU | 0 | 150 | 0 | 150
|  | Analog | TRUE |  | N_SFC_BP13IT01_PV |  |  | INT | %MW3912 | Motor Current |  | A | ###EU | 0 | 100 | 0 | 100
|  | Analog | TRUE |  | N_SFC_BP13LT01_PV |  |  | INT | %MW3913 | Bore Level |  | % | ###EU | 0 | 100 | 0 | 100
|  | Analog | TRUE |  | N_SFC_BP13PT01_PV |  |  | INT | %MW3914 | Discharge Pressure |  | kPa | ###EU | 0 | 100 | 0 | 100
|  | Analog |  |  | N_SFC_BP13FT01_YLDCD |  |  | INT | %MW3916 | Flow Yield Current Day |  | m³ | #####EU | 0 | 10000 | 0 | 10000
|  | Analog |  |  | N_SFC_BP13FT01_YLDPD |  |  | INT | %MW3917 | Flow Yield Previous Day |  | m³ | #####EU | 0 | 10000 | 0 | 10000
|  | Analog |  |  | N_SFC_BP13_HRSCD |  |  | INT | %MW3918 | Run Hours Current Day |  | Hrs | #.##EU | 0 | 2400 | 0 | 24
|  | Analog |  |  | N_SFC_BP13_HRSPD |  |  | INT | %MW3919 | Run Hours Previous Day |  | Hrs | #.##EU | 0 | 2400 | 0 | 24
|  | Analog |  |  | N_SFC_BP13FT01_YLD |  |  | LONG | %MW3922 | Flow Total Accumulated Yield |  | m³ | #########EU | 0 | 1000000000 | 0 | 1000000000
|  | Analog |  |  | N_SFC_BP13_HRS |  |  | LONG | %MW3924 | Total Accumulated Run Hours |  | Hrs | ########EU | 0 | 240000000 | 0 | 2400000
|  | Analog |  |  | N_SFC_BP13_ALM1 |  |  | INT | %MW3926 | Alarm Word 1
|  | Analog |  |  | N_SFC_BP13_ALM2 |  |  | INT | %MW3927 | Alarm Word 2
|  | Analog | TRUE |  | N_SFC_BP13_IA |  |  | INT | %MW3928 | Phase A Current |  | A | ###EU | 0 | 500 | 0 | 500
|  | Analog | TRUE |  | N_SFC_BP13_IB |  |  | INT | %MW3929 | Phase B Current |  | A | ###EU | 0 | 500 | 0 | 500
|  | Analog | TRUE |  | N_SFC_BP13_IC |  |  | INT | %MW3930 | Phase C Current |  | A | ###EU | 0 | 500 | 0 | 500
|  | Analog | TRUE |  | N_SFC_BP13_IE |  |  | INT | %MW3931 | Ground Current |  | mA | ###EU | 0 | 100 | 0 | 100
|  | Analog | TRUE |  | N_SFC_BP13_TC |  |  | INT | %MW3932 | Thermal Capacity |  | % | ###EU | 0 | 100 | 0 | 100
|  | Analog | TRUE |  | N_SFC_BP13_II |  |  | INT | %MW3933 | Current Phase Imbalance |  | % | ###EU | 0 | 100 | 0 | 100
|  | Analog | TRUE |  | N_SFC_BP13_LOAD |  |  | INT | %MW3934 | Full Load Current |  | % | ###EU | 0 | 100 | 0 | 100
|  | Analog | TRUE |  | N_SFC_BP13_PWR |  |  | INT | %MW3935 | Power |  | kW | ##.# | 0 | 1000 | 0 | 100
|  | Analog | TRUE |  | N_SFC_BP13_Volts |  |  | INT | %MW3936 | Voltage |  | V | ###EU | 0 | 500 | 0 | 500
|  | Analog |  |  | N_SFC_BP13_COT |  |  | INT | %MW3937 | Cause of Trip
|  | Analog |  |  | N_SFC_BP13_RST_TM |  |  | INT | %MW3938 | Time to Rest
|  | Analog | TRUE |  | N_SFC_BP13_PRETRIP_A |  |  | INT | %MW3939 | Phase A Pre-Trip Current |  | A | ###EU | 0 | 500 | 0 | 500
|  | Analog | TRUE |  | N_SFC_BP13_PRETRIP_B |  |  | INT | %MW3940 | Phase B Pre-Trip Current |  | A | ###EU | 0 | 500 | 0 | 500
|  | Analog | TRUE |  | N_SFC_BP13_PRETRIP_C |  |  | INT | %MW3941 | Phase C Pre-Trip Current |  | A | ###EU | 0 | 500 | 0 | 500
|  | Analog | TRUE |  | N_SFC_BP13_PRETRIP_GND |  |  | INT | %MW3942 | Ground Pre-Trip Current |  | mA | ###EU | 0 | 100 | 0 | 100
|  | Analog |  |  | N_SFC_BP13_FORCES_CNT |  |  | INT | %MW3948 | Number of Forces in PLC |  |  |  | 0 | 32767 | 0 | 32767
|  | Totalisers |  |  | N_SFC_BP13FT01_TOT.CurrDay |  |  | INT | %MW10240 | Current Day's Value |  | m³ | #####EU | 0 | 32767 | 0 | 32767
|  | Totalisers |  |  | N_SFC_BP13FT01_TOT.PrevDay |  |  | INT | %MW10241 | Previous Day's Value |  | m³ | #####EU | 0 | 32767 | 0 | 32767
|  | Totalisers |  |  | N_SFC_BP13FT01_TOT.CurrMonth |  |  | LONG | %MW10242 | Current Month's Value |  | m³ | #########EU | 0 | 1000000000 | 0 | 1000000000
|  | Totalisers |  |  | N_SFC_BP13FT01_TOT.PrevMonth |  |  | LONG | %MW10244 | Previous Month's Value |  | m³ | #########EU | 0 | 1000000000 | 0 | 1000000000
|  | Totalisers |  |  | N_SFC_BP13FT01_TOT.CurrYear |  |  | LONG | %MW10246 | Current Year's Value |  | m³ | #########EU | 0 | 1000000000 | 0 | 1000000000
|  | Totalisers |  |  | N_SFC_BP13FT01_TOT.PrevYear |  |  | LONG | %MW10248 | Previous Month's Value |  | m³ | #########EU | 0 | 1000000000 | 0 | 1000000000
|  | Totalisers |  |  | N_SFC_BP13HRS_TOT.CurrDay |  |  | INT | %MW10250 | Current Day's Value |  | Hrs | #.##EU | 0 | 2400 | 0 | 24
|  | Totalisers |  |  | N_SFC_BP13HRS_TOT.PrevDay |  |  | INT | %MW10251 | Previous Day's Value |  | Hrs | #.##EU | 0 | 2400 | 0 | 24
|  | Totalisers |  |  | N_SFC_BP13HRS_TOT.CurrMonth |  |  | LONG | %MW10252 | Current Month's Value |  | Hrs | ########EU | 0 | 240000000 | 0 | 2400000
|  | Totalisers |  |  | N_SFC_BP13HRS_TOT.PrevMonth |  |  | LONG | %MW10254 | Previous Month's Value |  | Hrs | ########EU | 0 | 240000000 | 0 | 2400000
|  | Totalisers |  |  | N_SFC_BP13HRS_TOT.CurrYear |  |  | LONG | %MW10256 | Current Year's Value |  | Hrs | ########EU | 0 | 240000000 | 0 | 2400000
|  | Totalisers |  |  | N_SFC_BP13HRS_TOT.PrevYear |  |  | LONG | %MW10258 | Previous Month's Value |  | Hrs | ########EU | 0 | 240000000 | 0 | 2400000
[5 empty] | C_SFC_BP13_ALMACK |  | CICODESVR | INT | LabelRetValue | Reset Command
[5 empty] | C_SFC_BP13_AUTO |  | CICODESVR | INT | LabelRetValue | Auto Command
[5 empty] | C_SFC_BP13_MAN |  | CICODESVR | INT | LabelRetValue | Manual Command
[5 empty] | C_SFC_BP13_LOCAL |  | CICODESVR | INT | LabelRetValue | Local Command
[5 empty] | C_SFC_BP13_OTM |  | CICODESVR | INT | LabelRetValue | Out to Maint Command
[5 empty] | C_SFC_BP13_OFF |  | CICODESVR | INT | LabelRetValue | Off Command
[5 empty] | C_SFC_BP13_STT |  | CICODESVR | INT | LabelRetValue | Start Command
[5 empty] | C_SFC_BP13_STP |  | CICODESVR | INT | LabelRetValue | Stop Command
[5 empty] | C_SFC_BP13_COMMSINHIBIT |  | CICODESVR | INT | LabelRetValue | Inhbit Comms Command
|  | Analog |  |  | N_SFC_BP13_FEST |  | memdevice | INT |  | Flow Estimate |  | m³/Hr | ###EU | 0 | 500 | 0 | 500

## Bore Pump Rev A
Equipment | Item Name | Tag Type | Set Trend | Category | Tag Name | Cluster Name | I/O Device | Data Type | Address | Comment | Deadband | Eng Units | Format | Raw Zero Scale | Raw Full Scale | Eng Zero Scale | Eng Full Scale | Custom 1 | Custom 2 | Custom 3 | Custom 4 | Custom 5 | Custom 6 | Custom 7 | Custom 8 | Historize | Project | EDITCODE | LINKED | OID | REF1 | REF2 | CUSTOM | TAGGENLINK
[5 empty] | Alarm |  |  |  | 10096
[5 empty] | Analog |  |  |  | 3461
[5 empty] | Status |  |  |  | 1096
[5 empty] | Totalisers |  |  |  | 10060
SFC_BP04 |  | Status |  |  | S_SFC_BP04_CLDWN |  |  | DIGITAL | %M1096 | Cooling Down
|  | Status |  |  | S_SFC_BP04_AUTO |  |  | DIGITAL | %M1097 | Auto
|  | Status |  |  | S_SFC_BP04_MAN |  |  | DIGITAL | %M1098 | Manual
|  | Status |  |  | S_SFC_BP04_LOCAL |  |  | DIGITAL | %M1099 | Local
|  | Status |  |  | S_SFC_BP04_OTM |  |  | DIGITAL | %M1100 | Out to Maintenance
|  | Status |  |  | S_SFC_BP04_OFF |  |  | DIGITAL | %M1101 | Off
|  | Status |  |  | S_SFC_BP04_RDY |  |  | DIGITAL | %M1102 | Ready
|  | Status |  |  | S_SFC_BP04_RUNNG |  |  | DIGITAL | %M1103 | Running
|  | Status |  |  | S_SFC_BP04_BIT1 |  |  | DIGITAL | %M1104 | Status Bit 1
|  | Status |  |  | S_SFC_BP04_BIT2 |  |  | DIGITAL | %M1105 | Status Bit 2
|  | Status |  |  | S_SFC_BP04_BIT3 |  |  | DIGITAL | %M1106 | Status Bit 3
|  | Status |  |  | S_SFC_BP04_BIT4 |  |  | DIGITAL | %M1107 | Status Bit 4
|  | Status |  |  | S_SFC_BP04MOTOR_HLTY |  |  | DIGITAL | %M1108 | Motor Healthy
|  | Status |  |  | S_SFC_BP04LOS_HLTY |  |  | DIGITAL | %M1109 | Emergency Stop Healthy
|  | Status |  |  | S_SFC_BP04_REMRDY |  |  | DIGITAL | %M1110 | Remote Ready
|  | Status |  |  | S_SFC_BP04POWER_ON |  |  | DIGITAL | %M1111 | Mains Power On
|  | Status |  |  | S_SFC_BP04_COMMSINHIBIT |  |  | DIGITAL | %M1112 | Communication Inhibited
|  | Alarm |  | TP_CRIT_CAT | A_SFC_BP04FT01_LO |  |  | DIGITAL | %M10096 | Low Flow
|  | Alarm |  | TP_CRIT_CAT | A_SFC_BP04CA1_FTO |  |  | DIGITAL | %M10097 | Contactor Failed to Open
|  | Alarm |  | TP_CRIT_CAT | A_SFC_BP04CA1_FTC |  |  | DIGITAL | %M10098 | Contactor Failed to Close
|  | Alarm |  | TP_CRIT_CAT | A_SFC_BP04MOTOR_FLT |  |  | DIGITAL | %M10099 | Motor Fault
|  | Alarm |  | TP_CRIT_CAT | A_SFC_BP04LOS_FLT |  |  | DIGITAL | %M10100 | Emergency Stop Fault
|  | Alarm |  | TP_CRIT_CAT | A_SFC_BP04POWER_FAIL |  |  | DIGITAL | %M10101 | Mains Power Fault
|  | Alarm |  | TP_CRIT_CAT | A_SFC_BP04_R0S1_FLT |  |  | DIGITAL | %M10102 | PLC Rack 0 Slot 1 Fault
|  | Alarm |  | TP_CRIT_CAT | A_SFC_BP04_R0S2_FLT |  |  | DIGITAL | %M10103 | PLC Rack 0 Slot 2 Fault
|  | Alarm |  | TP_CRIT_CAT | A_SFC_BP04FT01_BPV |  |  | DIGITAL | %M10104 | Flow Transmitter Error
|  | Alarm |  | TP_CRIT_CAT | A_SFC_BP04IT01_BPV |  |  | DIGITAL | %M10105 | Current Transmitter Error
|  | Alarm |  | TP_CRIT_CAT | A_SFC_BP04LT01_BPV |  |  | DIGITAL | %M10106 | Level Transmitter Error
|  | Alarm |  | TP_CRIT_CAT | A_SFC_BP04PT01_BPV |  |  | DIGITAL | %M10107 | Pressure Transmitter Error
|  | Alarm |  | TP_CRIT_CAT | A_SFC_BP04_ETH_RST |  |  | DIGITAL | %M10108 | PLC Ethernet Port Successfully Reset
|  | Alarm |  | TP_CRIT_CAT | A_SFC_BP04_PROJ |  |  | DIGITAL | %M10109 | PLC Project has Changed
|  | Alarm |  | TP_CRIT_CAT | A_SFC_BP04_FORCES |  |  | DIGITAL | %M10110 | PLC Number of Forces has Changed
|  | Alarm |  | TP_COMMS_CAT | A_SFC_BP04_COMMS |  |  | DIGITAL | %M10111 | Comms HB Timeout
|  | Analog | TRUE |  | N_SFC_BP04FT01_PV |  |  | INT | %MW3461 | Discharge Flow |  | m³/Hr | ###EU | 0 | 150 | 0 | 150
|  | Analog | TRUE |  | N_SFC_BP04IT01_PV |  |  | INT | %MW3462 | Motor Current |  | A | ###EU | 0 | 100 | 0 | 100
|  | Analog | TRUE |  | N_SFC_BP04LT01_PV |  |  | INT | %MW3463 | Bore Level |  | % | ###EU | 0 | 100 | 0 | 100
|  | Analog | TRUE |  | N_SFC_BP04PT01_PV |  |  | INT | %MW3464 | Discharge Pressure |  | kPa | ###EU | 0 | 100 | 0 | 100
|  | Analog |  |  | N_SFC_BP04FT01_YLDCD |  |  | INT | %MW3466 | Flow Yield Current Day |  | m³ | #####EU | 0 | 10000 | 0 | 10000
|  | Analog |  |  | N_SFC_BP04FT01_YLDPD |  |  | INT | %MW3467 | Flow Yield Previous Day |  | m³ | #####EU | 0 | 10000 | 0 | 10000
|  | Analog |  |  | N_SFC_BP04_HRSCD |  |  | INT | %MW3468 | Run Hours Current Day |  | Hrs | #.##EU | 0 | 2400 | 0 | 24
|  | Analog |  |  | N_SFC_BP04_HRSPD |  |  | INT | %MW3469 | Run Hours Previous Day |  | Hrs | #.##EU | 0 | 2400 | 0 | 24
|  | Analog |  |  | N_SFC_BP04FT01_YLD |  |  | LONG | %MW3472 | Flow Total Accumulated Yield |  | m³ | #########EU | 0 | 1000000000 | 0 | 1000000000
|  | Analog |  |  | N_SFC_BP04_HRS |  |  | LONG | %MW3474 | Total Accumulated Run Hours |  | Hrs | ########EU | 0 | 240000000 | 0 | 2400000
|  | Analog |  |  | N_SFC_BP04_FORCES_CNT |  |  | INT | %MW3498 | Number of Forces in PLC |  |  |  | 0 | 32767 | 0 | 32767
|  | Totalisers |  |  | N_SFC_BP04FT01_TOT.CurrDay |  |  | INT | %MW10060 | Current Day's Value |  | m³ | #####EU | 0 | 32767 | 0 | 32767
|  | Totalisers |  |  | N_SFC_BP04FT01_TOT.PrevDay |  |  | INT | %MW10061 | Previous Day's Value |  | m³ | #####EU | 0 | 32767 | 0 | 32767
|  | Totalisers |  |  | N_SFC_BP04FT01_TOT.CurrMonth |  |  | LONG | %MW10062 | Current Month's Value |  | m³ | #########EU | 0 | 1000000000 | 0 | 1000000000
|  | Totalisers |  |  | N_SFC_BP04FT01_TOT.PrevMonth |  |  | LONG | %MW10064 | Previous Month's Value |  | m³ | #########EU | 0 | 1000000000 | 0 | 1000000000
|  | Totalisers |  |  | N_SFC_BP04FT01_TOT.CurrYear |  |  | LONG | %MW10066 | Current Year's Value |  | m³ | #########EU | 0 | 1000000000 | 0 | 1000000000
|  | Totalisers |  |  | N_SFC_BP04FT01_TOT.PrevYear |  |  | LONG | %MW10068 | Previous Month's Value |  | m³ | #########EU | 0 | 1000000000 | 0 | 1000000000
|  | Totalisers |  |  | N_SFC_BP04HRS_TOT.CurrDay |  |  | INT | %MW10070 | Current Day's Value |  | Hrs | #.##EU | 0 | 2400 | 0 | 24
|  | Totalisers |  |  | N_SFC_BP04HRS_TOT.PrevDay |  |  | INT | %MW10071 | Previous Day's Value |  | Hrs | #.##EU | 0 | 2400 | 0 | 24
|  | Totalisers |  |  | N_SFC_BP04HRS_TOT.CurrMonth |  |  | LONG | %MW10072 | Current Month's Value |  | Hrs | ########EU | 0 | 240000000 | 0 | 2400000
|  | Totalisers |  |  | N_SFC_BP04HRS_TOT.PrevMonth |  |  | LONG | %MW10074 | Previous Month's Value |  | Hrs | ########EU | 0 | 240000000 | 0 | 2400000
|  | Totalisers |  |  | N_SFC_BP04HRS_TOT.CurrYear |  |  | LONG | %MW10076 | Current Year's Value |  | Hrs | ########EU | 0 | 240000000 | 0 | 2400000
|  | Totalisers |  |  | N_SFC_BP04HRS_TOT.PrevYear |  |  | LONG | %MW10078 | Previous Month's Value |  | Hrs | ########EU | 0 | 240000000 | 0 | 2400000
[5 empty] | C_SFC_BP04_ALMACK |  | CICODESVR | INT | LabelRetValue | Reset Command
[5 empty] | C_SFC_BP04_AUTO |  | CICODESVR | INT | LabelRetValue | Auto Command
[5 empty] | C_SFC_BP04_MAN |  | CICODESVR | INT | LabelRetValue | Manual Command
[5 empty] | C_SFC_BP04_LOCAL |  | CICODESVR | INT | LabelRetValue | Local Command
[5 empty] | C_SFC_BP04_OTM |  | CICODESVR | INT | LabelRetValue | Out to Maint Command
[5 empty] | C_SFC_BP04_OFF |  | CICODESVR | INT | LabelRetValue | Off Command
[5 empty] | C_SFC_BP04_STT |  | CICODESVR | INT | LabelRetValue | Start Command
[5 empty] | C_SFC_BP04_STP |  | CICODESVR | INT | LabelRetValue | Stop Command
[5 empty] | C_SFC_BP04_COMMSINHIBIT |  | CICODESVR | INT | LabelRetValue | Inhbit Comms Command
|  | Analog |  |  | N_SFC_BP04_FEST |  | memdevice | INT |  | Flow Estimate |  | m³/Hr | ###EU | 0 | 500 | 0 | 500

## Line Pump Rev A
Equipment | Item Name | Tag Type | Set Trend | Category | Tag Name | Cluster Name | I/O Device | Data Type | Address | Comment | Deadband | Eng Units | Format | Raw Zero Scale | Raw Full Scale | Eng Zero Scale | Eng Full Scale | Custom 1 | Custom 2 | Custom 3 | Custom 4 | Custom 5 | Custom 6 | Custom 7 | Custom 8 | Historize | Project | EDITCODE | LINKED | OID | REF1 | REF2 | CUSTOM | TAGGENLINK
[5 empty] | Alarm |  |  |  | 10500
[5 empty] | Analog |  |  |  | 5701
[5 empty] | Status |  |  |  | 2000
[5 empty] | Totalisers |  |  |  | 10700
SFC_LP1 |  | Alarm |  | TP_CRIT_CAT | A_SFC_LP1_24VDC_FLT |  |  | DIGITAL | %M10500 | MMII 24VDC Failed | [16 empty] | TP_Common |  |  | 0x028084b8
|  | Alarm |  | TP_COMMS_CAT | A_SFC_LP1MMII_COMMS |  |  | DIGITAL | %M10501 | MMII Communications Failed | [16 empty] | TP_Common |  |  | 0x028084b9
|  | Alarm |  | TP_CRIT_CAT | A_SFC_LP1MMII_TRIP |  |  | DIGITAL | %M10502 | MMII Tripped | [16 empty] | TP_Common | 55300 | 1 | 0x02804430 | DtEiYA@@
|  | Alarm |  | TP_CRIT_CAT | A_SFC_LP1_MOTOR_FLT |  |  | DIGITAL | %M10503 | MMII Motor Fault | [16 empty] | TP_Common | 55300 | 1 | 0x02804440 | t}Y_CA@@
|  | Alarm |  | TP_CRIT_CAT | A_SFC_LP1_PHASE_FLT |  |  | DIGITAL | %M10504 | MMII Phase | [16 empty] | TP_Common | 55300 | 1 | 0x02804450 | gxXCC@@
|  | Alarm |  | TP_COMMS_CAT | A_SFC_LP1_RTD_COMMS |  |  | DIGITAL | %M10505 | RTD Communications Failed | [16 empty] | TP_Common | 55300 | 1 | 0x02804460 | D.TsgA@@
|  | Alarm |  | TP_CRIT_CAT | A_SFC_LP1CA1_FTO |  |  | DIGITAL | %M10506 | Failed to Stop | [16 empty] | TP_Common | 55300 | 1 | 0x02804470 | Znp_o@@@
|  | Alarm |  | TP_CRIT_CAT | A_SFC_LP1CA1_FTC |  |  | DIGITAL | %M10507 | Failed to Start | [16 empty] | TP_Common | 55300 | 1 | 0x02804480 | s.i_q@@@
|  | Alarm |  | TP_CRIT_CAT | A_SFC_LP1_TMS |  |  | DIGITAL | %M10508 | Too Many Starts | [16 empty] | TP_Common | 55300 | 1 | 0x02804490 | wCuqUB@@
|  | Alarm |  | TP_CRIT_CAT | A_SFC_LP1CA1_FLT |  |  | DIGITAL | %M10509 | MMII Auxilliary Contactor | [16 empty] | TP_Common | 55300 | 1 | 0x028044a0 | ^bypSC@@
|  | Alarm |  | TP_CRIT_CAT | A_SFC_LP1ISOL_FLT |  |  | DIGITAL | %M10510 | MMII Isolator | [16 empty] | TP_Common | 55300 | 1 | 0x028044b0 | ^baosA@@
|  | Alarm |  | TP_CRIT_CAT | A_SFC_LP1LOS_FLT |  |  | DIGITAL | %M10511 | MMII Emergency Stop | [16 empty] | TP_Common | 55300 | 1 | 0x028044c0 | ii@t~C@@
|  | Alarm |  | TP_CRIT_CAT | A_SFC_LP1RTD_HH |  |  | DIGITAL | %M10512 | RTD Temperature Trip | [16 empty] | TP_Common | 55300 | 1 | 0x028044d0 | bz\k.C@@
|  | Alarm |  | TP_CRIT_CAT | A_SFC_LP1RTD_HI |  |  | DIGITAL | %M10513 | RTD Temperature High | [16 empty] | TP_Common | 55300 | 1 | 0x028044e0 | s\pEM@@@
|  | Alarm |  | TP_CRIT_CAT | A_SFC_LP1THERM_FLT |  |  | DIGITAL | %M10514 | MMII Thermistor | [16 empty] | TP_Common | 55300 | 1 | 0x028044f0 | f^c^fA@@
|  | Alarm |  | TP_CRIT_CAT | A_SFC_LP1TOL_FLT |  |  | DIGITAL | %M10515 | MMII Thermal Overload Fault | [16 empty] | TP_Common | 55300 | 1 | 0x02804500 | R¦w.C@@
|  | Alarm |  | TP_CRIT_CAT | A_SFC_LP1UNDC_FLT |  |  | DIGITAL | %M10516 | MMII Under Current | [16 empty] | TP_Common | 55300 | 1 | 0x02804510 | ¦wmttA@@
|  | Alarm |  | TP_CRIT_CAT | A_SFC_LP1MMII_GEN |  |  | DIGITAL | %M10517 | MMII General Fault | [16 empty] | TP_Common | 55300 | 1 | 0x02804520 | pZcAzA@@
|  | Alarm |  | TP_CRIT_CAT | A_SFC_LP1MMII_FLT |  |  | DIGITAL | %M10518 | MMII Fault | [16 empty] | TP_Common | 55300 | 1 | 0x02806bf6 | avpB@@
|  | Status |  |  | S_SFC_LP1_24VDC_HLTY |  |  | DIGITAL | %M2000 | MMII 24VDC Healthy
|  | Status |  |  | S_SFC_LP1_AUTO |  |  | DIGITAL | %M2001 | Auto Status | [16 empty] | TP_Common | 55300 | 1 | 0x02806bf7 | HRc\HB@@
|  | Status |  |  | S_SFC_LP1_BIT1 |  |  | DIGITAL | %M2002 | Status Bit 1 | [16 empty] | TP_Common | 55300 | 1 | 0x02806bf8 | Kk\Ye@@@
|  | Status |  |  | S_SFC_LP1_BIT2 |  |  | DIGITAL | %M2003 | Status Bit 2 | [16 empty] | TP_Common | 55300 | 1 | 0x02806bf9 | GeleOA@@
|  | Status |  |  | S_SFC_LP1_BIT3 |  |  | DIGITAL | %M2004 | Status Bit 3 | [16 empty] | TP_Common | 55300 | 1 | 0x02806bfa | D`.W¦B@@
|  | Status |  |  | S_SFC_LP1_BIT4 |  |  | DIGITAL | %M2005 | Status Bit 4 | [16 empty] | TP_Common | 55300 | 1 | 0x02806bfb | UugEoB@@
|  | Status |  |  | S_SFC_LP1_CILK |  |  | DIGITAL | %M2006 | Critical Interlock | [16 empty] | TP_Common | 55300 | 1 | 0x02806bfc | UmfskB@@
|  | Status |  |  | S_SFC_LP1_CLDWN |  |  | DIGITAL | %M2007 | Cooling Down Status | [16 empty] | TP_Common | 55300 | 1 | 0x02806bfd | D.xhWB@@
|  | Status |  |  | S_SFC_LP1_DUTY |  |  | DIGITAL | %M2008 | Duty Status | [16 empty] | TP_Common | 55300 | 1 | 0x02806bfe | GdsPB@@
|  | Status |  |  | S_SFC_LP1_FLTD |  |  | DIGITAL | %M2009 | Fault Status
|  | Status |  |  | S_SFC_LP1_LOCAL |  |  | DIGITAL | %M2010 | Local Status | [16 empty] | TP_Common | 55300 | 1 | 0x02806bff | CBui\C@@
|  | Status |  |  | S_SFC_LP1_MAN |  |  | DIGITAL | %M2011 | Manual Status | [16 empty] | TP_Common | 55300 | 1 | 0x02806c00 | xtmAO@@@
|  | Status |  |  | S_SFC_LP1MMII_AUTO |  |  | DIGITAL | %M2012 | MMII Auto Status | [16 empty] | TP_Common | 55300 | 1 | 0x02806c01 | @hJoxB@@
|  | Status |  |  | S_SFC_LP1MMII_MAN |  |  | DIGITAL | %M2013 | MMII Manual Status | [16 empty] | TP_Common | 55300 | 1 | 0x02806c02 | @TMAdC@@
|  | Status |  |  | S_SFC_LP1MMII_RUNNG |  |  | DIGITAL | %M2014 | MMII Run Status
|  | Status |  |  | S_SFC_LP1MMII_TRIPStat |  |  | DIGITAL | %M2015 | MMII Trip Status
|  | Status |  |  | S_SFC_LP1MMII_NCILK |  |  | DIGITAL | %M2016 | MMII Non Critical Interlock
|  | Status |  |  | S_SFC_LP1_OFF |  |  | DIGITAL | %M2017 | Off Status | [16 empty] | TP_Common | 55300 | 1 | 0x02806c03 | G}DFIA@@
|  | Status |  |  | S_SFC_LP1_OTM |  |  | DIGITAL | %M2018 | Maintenance Status | [16 empty] | TP_Common | 55300 | 1 | 0x02806c04 | RPymC@@@
|  | Status |  |  | S_SFC_LP1_RDY |  |  | DIGITAL | %M2020 | Ready Status | [16 empty] | TP_Common | 55300 | 1 | 0x028057e0 | @T}jeC@@
|  | Status |  |  | S_SFC_LP1_RUNNG |  |  | DIGITAL | %M2021 | Running Status | [16 empty] | TP_Common | 55300 | 1 | 0x028057f0 | CZLXVB@@
|  | Status |  |  | S_SFC_LP1_STBY |  |  | DIGITAL | %M2023 | Standby Status | [16 empty] | TP_Common | 55300 | 1 | 0x02805800 | jkaGrA@@
|  | Status |  |  | S_SFC_LP1CA1_CLSD |  |  | DIGITAL | %M2025 | MMII Contactor Closed | [16 empty] | TP_Common | 55300 | 1 | 0x02805810 | aXRjI@@@
|  | Status |  |  | S_SFC_LP1MMII_GENStat |  |  | DIGITAL | %M2040 | MMII General Fault Status | [16 empty] | TP_Common | 55300 | 1 | 0x02805820 | UzvtPB@@
|  | Status |  |  | S_SFC_LP1MMII_FLTStat |  |  | DIGITAL | %M2041 | MMII Fault Status | [16 empty] | TP_Common | 55300 | 1 | 0x02805830 | wHEkU@@@
|  | Analog |  |  | N_SFC_LP1_ALM1 |  |  | INT | %MW5701 | Alarm Word 1 |  |  |  | 0 | 32766 | 0 | 32766 | [9 empty] | TP_Common | 55300 | 1 | 0x02805840 | UrvtPB@@
|  | Analog |  |  | N_SFC_LP1_ALM2 |  |  | INT | %MW5702 | Alarm Word 2 |  |  |  | 0 | 32766 | 0 | 32766 | [9 empty] | TP_Common | 55300 | 1 | 0x02805850 | wXKCWA@@
|  | Analog | TRUE |  | N_SFC_LP1_IA |  |  | INT | %MW5703 | Motor Current A |  | A | ###EU | 0 | 350 | 0 | 500 | [9 empty] | TP_Common | 55300 | 1 | 0x02805870 | zmxA@@
|  | Analog | TRUE |  | N_SFC_LP1_IB |  |  | INT | %MW5704 | Motor Current B |  | A | ###EU | 0 | 350 | 0 | 500 | [9 empty] | TP_Common | 55300 | 1 | 0x02805880 | RdaEAA@@
|  | Analog | TRUE |  | N_SFC_LP1_IC |  |  | INT | %MW5705 | Motor Current C |  | A | ###EU | 0 | 350 | 0 | 500 | [9 empty] | TP_Common | 55300 | 1 | 0x02805890 | UzvtPB@@
|  | Analog | TRUE |  | N_SFC_LP1_IE |  |  | INT | %MW5706 | Motor Leakage Current |  | mA | ###EU | 0 | 100 | 0 | 100 | [9 empty] | TP_Common | 55300 | 1 | 0x028058a0 | {rkXdA@@
|  | Analog | TRUE |  | N_SFC_LP1_TC |  |  | INT | %MW5707 | Thermal Capacity |  | % | ###EU | 0 | 100 | 0 | 100 | [9 empty] | TP_Common | 55300 | 1 | 0x028058b0 | D{yB`@@@
|  | Analog | TRUE |  | N_SFC_LP1_II |  |  | INT | %MW5708 | Motor Phase Current Imbalance |  | % | ###EU | 0 | 100 | 0 | 100 | [9 empty] | TP_Common | 55300 | 1 | 0x028058c0 | Y@ZhGA@@
|  | Analog | TRUE |  | N_SFC_LP1_LOAD |  |  | INT | %MW5709 | Motor Load %Flc |  | % | ###EU | 0 | 100 | 0 | 100
|  | Analog | TRUE |  | N_SFC_LP1_PWR |  |  | INT | %MW5710 | Motor Power Usage |  | kW | ##.# | 0 | 1000 | 0 | 100
|  | Analog | TRUE |  | N_SFC_LP1_Volts |  |  | INT | %MW5711 | Motor Voltage |  | V | ###EU | 0 | 500 | 0 | 500
|  | Analog |  |  | N_SFC_LP1_COT |  |  | INT | %MW5712 | Cause Of Trip Number |  |  |  | 0 | 32 | 0 | 32
|  | Analog |  |  | N_SFC_LP1_RST_TM |  |  | INT | %MW5713 | Reset Time |  |  |  | 0 | 32766 | 0 | 32766
|  | Analog | TRUE |  | N_SFC_LP1_PRETRIP_A |  |  | INT | %MW5714 | Pre-Trip Phase A Current |  | A | ###EU | 0 | 500 | 0 | 500
|  | Analog | TRUE |  | N_SFC_LP1_PRETRIP_B |  |  | INT | %MW5715 | Pre-Trip Phase B Current |  | A | ###EU | 0 | 500 | 0 | 500
|  | Analog | TRUE |  | N_SFC_LP1_PRETRIP_C |  |  | INT | %MW5716 | Pre-Trip Phase C Current |  | A | ###EU | 0 | 500 | 0 | 500
|  | Analog | TRUE |  | N_SFC_LP1_PRETRIP_GND |  |  | INT | %MW5717 | Pre-Trip Gnd Flt Leakage Current |  | mA | ###EU | 0 | 100 | 0 | 100
|  | Totalisers |  |  | N_SFC_LP1Hrs_TOT.CurrDay |  |  | INT | %MW10700 | Current Day's Hours Value |  | Hrs | #.##EU | 0 | 2400 | 0 | 24
|  | Totalisers |  |  | N_SFC_LP1Hrs_TOT.PrevDay |  |  | INT | %MW10701 | Previous Day's Hours Value |  | Hrs | #.##EU | 0 | 2400 | 0 | 24
|  | Totalisers |  |  | N_SFC_LP1Hrs_TOT.CurrMonth |  |  | LONG | %MW10702 | Current Month's Hours Value |  | Hrs | #########EU | 0 | 240000000 | 0 | 2400000
|  | Totalisers |  |  | N_SFC_LP1Hrs_TOT.PrevMonth |  |  | LONG | %MW10704 | Previous Month's Hours Value |  | Hrs | #########EU | 0 | 240000000 | 0 | 2400000
|  | Totalisers |  |  | N_SFC_LP1Hrs_TOT.CurrYear |  |  | LONG | %MW10706 | Current Years Hours Value |  | Hrs | #########EU | 0 | 240000000 | 0 | 2400000
|  | Totalisers |  |  | N_SFC_LP1Hrs_TOT.PrevYear |  |  | LONG | %MW10708 | Previous Years Hours Value |  | Hrs | #########EU | 0 | 240000000 | 0 | 2400000
|  | Totalisers |  |  | N_SFC_LP1Kwh_TOT.CurrDay |  |  | INT | %MW10900 | Current Day's kwh Value |  | kwh | #####EU | 0 | 32767 | 0 | 32767
|  | Totalisers |  |  | N_SFC_LP1Kwh_TOT.PrevDay |  |  | INT | %MW10901 | Previous Day's kwh Value |  | kwh | #####EU | 0 | 32767 | 0 | 32767
|  | Totalisers |  |  | N_SFC_LP1Kwh_TOT.CurrMonth |  |  | LONG | %MW10902 | Current Month's kwh Value |  | kwh | #########EU | 0 | 1000000000 | 0 | 1000000000
|  | Totalisers |  |  | N_SFC_LP1Kwh_TOT.PrevMonth |  |  | LONG | %MW10904 | Previous Month's kwh Value |  | kwh | #########EU | 0 | 1000000000 | 0 | 1000000000
|  | Totalisers |  |  | N_SFC_LP1Kwh_TOT.CurrYear |  |  | LONG | %MW10906 | Current Years kwh Value |  | kwh | #########EU | 0 | 1000000000 | 0 | 1000000000
|  | Totalisers |  |  | N_SFC_LP1Kwh_TOT.PrevYear |  |  | LONG | %MW10908 | Previous Years kwh Value |  | kwh | #########EU | 0 | 1000000000 | 0 | 1000000000
[5 empty] | C_SFC_LP1_ALMACK |  | CICODESVR | INT | LabelRetValue | Alarm Ack Command
[5 empty] | C_SFC_LP1_AUTO |  | CICODESVR | INT | LabelRetValue | Auto Command
[5 empty] | C_SFC_LP1_MAN |  | CICODESVR | INT | LabelRetValue | Manual Command
[5 empty] | C_SFC_LP1_LOCAL |  | CICODESVR | INT | LabelRetValue | Local Command
[5 empty] | C_SFC_LP1_OTM |  | CICODESVR | INT | LabelRetValue | Out Maint Command
[5 empty] | C_SFC_LP1_OFF |  | CICODESVR | INT | LabelRetValue | Off Command
[5 empty] | C_SFC_LP1_STT |  | CICODESVR | INT | LabelRetValue | Start Command
[5 empty] | C_SFC_LP1_STP |  | CICODESVR | INT | LabelRetValue | Stop Command
[5 empty] | C_SFC_LP1_DUTY |  | CICODESVR | INT | LabelRetValue | Duty Command
[5 empty] | C_SFC_LP1_STBY |  | CICODESVR | INT | LabelRetValue | Standby Command

## SFC
Equipment | Item Name | Tag Type | Set Trend | Category | Tag Name | Cluster Name | I/O Device | Data Type | Address | Comment | Deadband | Eng Units | Format | Raw Zero Scale | Raw Full Scale | Eng Zero Scale | Eng Full Scale | Custom 1 | Custom 2 | Custom 3 | Custom 4 | Custom 5 | Custom 6 | Custom 7 | Custom 8 | Historize | Project | EDITCODE | LINKED | OID | REF1 | REF2 | CUSTOM | TAGGENLINK
[5 empty] | Status |  |  |  | 2282
[5 empty] | Analog |  |  |  | 5656
[5 empty] | Alarm |  |  |  | 10785
[5 empty] | Totalisers |  |  |  | 10260
SFC_SFC |  | Analog |  |  | N_SFC_SFCLT02_SP |  |  | INT | %MW5656 | SFC Surge Vessel Level Setpoint |  | % | ###EU | 0 | 100 | 0 | 100
|  | Analog |  |  | N_SFC_SFCPT02_SP |  |  | INT | %MW5657 | SFC Surge Vessel Pressure Setpoint |  | kPa | ####EU | 0 | 2600 | 0 | 2600
|  | Analog | TRUE |  | N_SFC_SFCPT01_PV |  |  | INT | %MW5801 | SFC Line Pressure (kPa) |  | kPa | ####EU | 0 | 5500 | 0 | 5500
|  | Analog | TRUE |  | N_SFC_SFCPT02_PV |  |  | INT | %MW5802 | SFC Surge Vessel Pressure (kPa) |  | kPa | ####EU | 0 | 2600 | 0 | 2600
|  | Analog | TRUE |  | N_SFC_SFCLT01_PV |  |  | INT | %MW5803 | SFC Tank Level (%) |  | % | ###EU | 0 | 100 | 0 | 100
|  | Analog | TRUE |  | N_SFC_SFCLT02_PV |  |  | INT | %MW5808 | SFC Surge Vessel Level (%) |  | % | ###EU | 0 | 100 | 0 | 100
|  | Analog | TRUE |  | N_SFC_SFCFT01_PV |  |  | INT | %MW5809 | SFC Tank Calculated in Flow |  | m³/Hr | #####EU | 0 | 32000 | 0 | 32000
|  | Analog | TRUE |  | N_SFC_SFCLP1TT03_PV |  |  | INT | %MW5811 | P1 DE Bearing Temperature |  | °C | #### EU | 0 | 100 | 0 | 100
|  | Analog | TRUE |  | N_SFC_SFCLP1TT04_PV |  |  | INT | %MW5812 | P1 NDE Bearing Temperature |  | °C | #### EU | 0 | 32766 | 0 | 32766
|  | Analog | TRUE |  | N_SFC_SFCM1TT01_PV |  |  | INT | %MW5813 | P1 Motor NDE Bearing Temperature |  | °C | #### EU | 0 | 32766 | 0 | 32766
|  | Analog | TRUE |  | N_SFC_SFCM1TT02_PV |  |  | INT | %MW5814 | P1 Motor DE Bearing Temperature |  | °C | #### EU | 0 | 32766 | 0 | 32766
|  | Analog | TRUE |  | N_SFC_SFCLP2TT03_PV |  |  | INT | %MW5815 | P2 DE Bearing Temperature |  | °C | #### EU | 0 | 32766 | 0 | 32766
|  | Analog | TRUE |  | N_SFC_SFCLP2TT04_PV |  |  | INT | %MW5816 | P2 NDE Bearing Temperature |  | °C | #### EU | 0 | 32766 | 0 | 32766
|  | Analog | TRUE |  | N_SFC_SFCM2TT01_PV |  |  | INT | %MW5817 | P2 Motor NDE Bearing Temperature |  | °C | #### EU | 0 | 32766 | 0 | 32766
|  | Analog | TRUE |  | N_SFC_SFCM2TT02_PV |  |  | INT | %MW5818 | P2 Motor DE Bearing Temperature |  | °C | #### EU | 0 | 32766 | 0 | 32766
|  | Analog | TRUE |  | N_SFC_SFCLP3TT03_PV |  |  | INT | %MW5819 | P3 DE Bearing Temperature |  | °C | #### EU | 0 | 32766 | 0 | 32766
|  | Analog | TRUE |  | N_SFC_SFCLP3TT04_PV |  |  | INT | %MW5820 | P3 NDE Bearing Temperature |  | °C | #### EU | 0 | 32766 | 0 | 32766
|  | Analog | TRUE |  | N_SFC_SFCM3TT01_PV |  |  | INT | %MW5821 | P3 Motor NDE Bearing Temperature |  | °C | #### EU | 0 | 32766 | 0 | 32766
|  | Analog | TRUE |  | N_SFC_SFCM3TT02_PV |  |  | INT | %MW5822 | P3 Motor DE Bearing Temperature |  | °C | #### EU | 0 | 32766 | 0 | 32766
|  | Analog | TRUE |  | N_SFC_SFCLP4TT03_PV |  |  | INT | %MW5850 | P4 DE Bearing Temperature |  | °C | #### EU | 0 | 32766 | 0 | 32766
|  | Analog | TRUE |  | N_SFC_SFCLP4TT04_PV |  |  | INT | %MW5851 | P4 NDE Bearing Temperature |  | °C | #### EU | 0 | 32766 | 0 | 32766
|  | Analog | TRUE |  | N_SFC_SFCM4TT01_PV |  |  | INT | %MW5852 | P4 Motor NDE Bearing Temperature |  | °C | #### EU | 0 | 32766 | 0 | 32766
|  | Analog | TRUE |  | N_SFC_SFCM4TT02_PV |  |  | INT | %MW5853 | P4 Motor DE Bearing Temperature |  | °C | #### EU | 0 | 32766 | 0 | 32766
|  | Analog | TRUE |  | N_SFC_SFCLP5TT03_PV |  |  | INT | %MW5854 | P5 DE Bearing Temperature |  | °C | #### EU | 0 | 32766 | 0 | 32766
|  | Analog | TRUE |  | N_SFC_SFCLP5TT04_PV |  |  | INT | %MW5855 | P5 NDE Bearing Temperature |  | °C | #### EU | 0 | 32766 | 0 | 32766
|  | Analog | TRUE |  | N_SFC_SFCM5TT01_PV |  |  | INT | %MW5856 | P5 Motor NDE Bearing Temperature |  | °C | #### EU | 0 | 32766 | 0 | 32766
|  | Analog | TRUE |  | N_SFC_SFCM5TT02_PV |  |  | INT | %MW5857 | P5 Motor DE Bearing Temperature |  | °C | #### EU | 0 | 32766 | 0 | 32766
|  | Analog |  |  | N_SFC_SFCP1_HRSCD |  |  | INT | %MW5858 | P1 Current Day Accumulated Run Hours |  | Hrs | #.##EU | 0 | 2400 | 0 | 24
|  | Analog |  |  | N_SFC_SFCP1_HRSPD |  |  | INT | %MW5859 | P1 Previous Day Accumulated Run Hours |  | Hrs | #.##EU | 0 | 2400 | 0 | 24
|  | Analog |  |  | N_SFC_SFCP2_HRSCD |  |  | INT | %MW5860 | P2 Current Day Accumulated Run Hours |  | Hrs | #.##EU | 0 | 2400 | 0 | 24
|  | Analog |  |  | N_SFC_SFCP2_HRSPD |  |  | INT | %MW5861 | P2 Previous Day Accumulated Run Hours |  | Hrs | #.##EU | 0 | 2400 | 0 | 24
|  | Analog |  |  | N_SFC_SFCP3_HRSCD |  |  | INT | %MW5862 | P3 Current Day Accumulated Run Hours |  | Hrs | #.##EU | 0 | 2400 | 0 | 24
|  | Analog |  |  | N_SFC_SFCP3_HRSPD |  |  | INT | %MW5863 | P3 Previous Day Accumulated Run Hours |  | Hrs | #.##EU | 0 | 2400 | 0 | 24
|  | Analog |  |  | N_SFC_SFCP4_HRSCD |  |  | INT | %MW5864 | P4 Current Day Accumulated Run Hours |  | Hrs | #.##EU | 0 | 2400 | 0 | 24
|  | Analog |  |  | N_SFC_SFCP4_HRSPD |  |  | INT | %MW5865 | P4 Previous Day Accumulated Run Hours |  | Hrs | #.##EU | 0 | 2400 | 0 | 24
|  | Analog |  |  | N_SFC_SFCP5_HRSCD |  |  | INT | %MW5866 | P5 Current Day Accumulated Run Hours |  | Hrs | #.##EU | 0 | 2400 | 0 | 24
|  | Analog |  |  | N_SFC_SFCP5_HRSPD |  |  | INT | %MW5867 | P5 Previous Day Accumulated Run Hours |  | Hrs | #.##EU | 0 | 2400 | 0 | 24
|  | Analog |  |  | N_SFC_SFCP1_KWHCD |  |  | INT | %MW5868 | P1 Current Day Accumulated KWH |  | kWh | ####.#EU | 0 | 10000 | 0 | 1000
|  | Analog |  |  | N_SFC_SFCP1_KWHPD |  |  | INT | %MW5869 | P1 Previous Day Accumulated KWH |  | kWh | ####.#EU | 0 | 10000 | 0 | 1000
|  | Analog |  |  | N_SFC_SFCP2_KWHCD |  |  | INT | %MW5870 | P2 Current Day Accumulated KWH |  | kWh | ####.#EU | 0 | 10000 | 0 | 1000
|  | Analog |  |  | N_SFC_SFCP2_KWHPD |  |  | INT | %MW5871 | P2 Previous Day Accumulated KWH |  | kWh | ####.#EU | 0 | 10000 | 0 | 1000
|  | Analog |  |  | N_SFC_SFCP3_KWHCD |  |  | INT | %MW5872 | P3 Current Day Accumulated KWH |  | kWh | ####.#EU | 0 | 10000 | 0 | 1000
|  | Analog |  |  | N_SFC_SFCP3_KWHPD |  |  | INT | %MW5873 | P3 Previous Day Accumulated KWH |  | kWh | ####.#EU | 0 | 10000 | 0 | 1000
|  | Analog |  |  | N_SFC_SFCP4_KWHCD |  |  | INT | %MW5874 | P4 Current Day Accumulated KWH |  | kWh | ####.#EU | 0 | 10000 | 0 | 1000
|  | Analog |  |  | N_SFC_SFCP4_KWHPD |  |  | INT | %MW5875 | P4 Previous Day Accumulated KWH |  | kWh | ####.#EU | 0 | 10000 | 0 | 1000
|  | Analog |  |  | N_SFC_SFCP5_KWHCD |  |  | INT | %MW5876 | P5 Current Day Accumulated KWH |  | kWh | ####.#EU | 0 | 10000 | 0 | 1000
|  | Analog |  |  | N_SFC_SFCP5_KWHPD |  |  | INT | %MW5877 | P5 Previous Day Accumulated KWH |  | kWh | ####.#EU | 0 | 10000 | 0 | 1000
|  | Analog |  |  | N_SFC_SFCP1_HRS |  |  | LONG | %MW5880 | P1 Total Accum Run Hours |  | Hrs | ########EU | 0 | 240000000 | 0 | 2400000
|  | Analog |  |  | N_SFC_SFCP2_HRS |  |  | LONG | %MW5882 | P2 Total Accum Run Hours |  | Hrs | ########EU | 0 | 240000000 | 0 | 2400000
|  | Analog |  |  | N_SFC_SFCP3_HRS |  |  | LONG | %MW5884 | P3 Total Accum Run Hours |  | Hrs | ########EU | 0 | 240000000 | 0 | 2400000
|  | Analog |  |  | N_SFC_SFCP4_HRS |  |  | LONG | %MW5886 | P4 Total Accum Run Hours |  | Hrs | ########EU | 0 | 240000000 | 0 | 2400000
|  | Analog |  |  | N_SFC_SFCP5_HRS |  |  | LONG | %MW5888 | P5 Total Accum Run Hours |  | Hrs | ########EU | 0 | 240000000 | 0 | 2400000
|  | Analog |  |  | N_SFC_SFCP1_KWH |  |  | LONG | %MW5890 | P1 Total Accum KWH |  | kWh | ####.#EU
|  | Analog |  |  | N_SFC_SFCP2_KWH |  |  | LONG | %MW5892 | P2 Total Accum KWH |  | kWh | ####.#EU
|  | Analog |  |  | N_SFC_SFCP3_KWH |  |  | LONG | %MW5894 | P3 Total Accum KWH |  | kWh | ####.#EU
|  | Analog |  |  | N_SFC_SFCP4_KWH |  |  | LONG | %MW5896 | P4 Total Accum KWH |  | kWh | ####.#EU
|  | Analog |  |  | N_SFC_SFCP5_KWH |  |  | LONG | %MW5898 | P5 Total Accum KWH |  | kWh | ####.#EU
|  | Analog |  |  | N_SFC_SFCP1_STT_CNT |  |  | LONG | %MW5906 | P1 Auto Duty Rotation Start Count |  |  |  | 0 | 32766 | 0 | 32766
|  | Analog |  |  | N_SFC_SFCP2_STT_CNT |  |  | LONG | %MW5908 | P2 Auto Duty Rotation Start Count |  |  |  | 0 | 32766 | 0 | 32766
|  | Analog |  |  | N_SFC_SFCP3_STT_CNT |  |  | LONG | %MW5910 | P3 Auto Duty Rotation Start Count |  |  |  | 0 | 32766 | 0 | 32766
|  | Analog |  |  | N_SFC_SFCP4_STT_CNT |  |  | LONG | %MW5912 | P4 Auto Duty Rotation Start Count |  |  |  | 0 | 32766 | 0 | 32766
|  | Analog |  |  | N_SFC_SFCP5_STT_CNT |  |  | LONG | %MW5914 | P5 Auto Duty Rotation Start Count |  |  |  | 0 | 32766 | 0 | 32766
|  | Analog |  |  | N_SFC_SFCPT01_LO_SP |  |  | INT | %MW5960 | SFC Pumps Low Pressure Setpoint |  | kPa | ####EU | 0 | 5500 | 0 | 5500 | [9 empty] | TP_Common | 55300 | 1 | 0x028049e0 | idDA@@
|  | Analog |  |  | N_SFC_SFCLT01_HH_SP |  |  | INT | %MW5961 | SFC Tank High High Level Setpoint |  | % | ###EU | 0 | 100 | 0 | 100
|  | Analog |  |  | N_SFC_SFCLT01_LL_SP |  |  | INT | %MW5962 | SFC Tank Low Low Level Setpoint |  | % | ###EU | 0 | 100 | 0 | 100
|  | Analog |  |  | N_SFC_SFCCLDWN_SP |  |  | INT | %MW5963 | SFC Pumps Cool Down Time Setpoint |  | s | ###EU | 0 | 360 | 0 | 360
|  | Analog |  |  | N_SFC_SFCBP01_PRIO_SP |  |  | INT | %MW5964 | SFC Bore Pump BP01 Priority Setpoint |  |  |  | 0 | 32766 | 0 | 32766
|  | Analog |  |  | N_SFC_SFCBP02_PRIO_SP |  |  | INT | %MW5965 | SFC Bore Pump BP02 Priority Setpoint |  |  |  | 0 | 32766 | 0 | 32766
|  | Analog |  |  | N_SFC_SFCBP03_PRIO_SP |  |  | INT | %MW5966 | SFC Bore Pump BP03 Priority Setpoint |  |  |  | 0 | 32766 | 0 | 32766
|  | Analog |  |  | N_SFC_SFCBP04_PRIO_SP |  |  | INT | %MW5967 | SFC Bore Pump BP04 Priority Setpoint |  |  |  | 0 | 32766 | 0 | 32766
|  | Analog |  |  | N_SFC_SFCBP05_PRIO_SP |  |  | INT | %MW5968 | SFC Bore Pump BP05 Priority Setpoint |  |  |  | 0 | 32766 | 0 | 32766
|  | Analog |  |  | N_SFC_SFCBP06_PRIO_SP |  |  | INT | %MW5969 | SFC Bore Pump BP06 Priority Setpoint |  |  |  | 0 | 32766 | 0 | 32766
|  | Analog |  |  | N_SFC_SFCBP07_PRIO_SP |  |  | INT | %MW5970 | SFC Bore Pump BP07 Priority Setpoint |  |  |  | 0 | 32766 | 0 | 32766
|  | Analog |  |  | N_SFC_SFCBP08_PRIO_SP |  |  | INT | %MW5971 | SFC Bore Pump BP08 Priority Setpoint |  |  |  | 0 | 32766 | 0 | 32766
|  | Analog |  |  | N_SFC_SFCBP09_PRIO_SP |  |  | INT | %MW5972 | SFC Bore Pump BP09 Priority Setpoint |  |  |  | 0 | 32766 | 0 | 32766
|  | Analog |  |  | N_SFC_SFCBP10_PRIO_SP |  |  | INT | %MW5973 | SFC Bore Pump BP10 Priority Setpoint |  |  |  | 0 | 32766 | 0 | 32766
|  | Analog |  |  | N_SFC_SFCBP11_PRIO_SP |  |  | INT | %MW5974 | SFC Bore Pump BP11 Priority Setpoint |  |  |  | 0 | 32766 | 0 | 32766
|  | Analog |  |  | N_SFC_SFCBP12_PRIO_SP |  |  | INT | %MW5975 | SFC Bore Pump BP12 Priority Setpoint |  |  |  | 0 | 32766 | 0 | 32766
|  | Analog |  |  | N_SFC_SFCBP13_PRIO_SP |  |  | INT | %MW5976 | SFC Bore Pump BP13 Priority Setpoint |  |  |  | 0 | 32766 | 0 | 32766
|  | Analog |  |  | N_SFC_SFCLT01_STT_SP1 |  |  | INT | %MW5977 | SFC Tank Level Bore Control Priority Setpoint 1 |  | % | ###EU | 0 | 100 | 0 | 100
|  | Analog |  |  | N_SFC_SFCLT01_STT_SP2 |  |  | INT | %MW5978 | SFC Tank Level Bore Control Priority Setpoint 2 |  | % | ###EU | 0 | 100 | 0 | 100
|  | Analog |  |  | N_SFC_SFCLT01_STT_SP3 |  |  | INT | %MW5979 | SFC Tank Level Bore Control Priority Setpoint 3 |  | % | ###EU | 0 | 100 | 0 | 100
|  | Analog |  |  | N_SFC_SFCLT01_STT_SP4 |  |  | INT | %MW5980 | SFC Tank Level Bore Control Priority Setpoint 4 |  | % | ###EU | 0 | 100 | 0 | 100
|  | Analog |  |  | N_SFC_SFCLT01_STT_SP5 |  |  | INT | %MW5981 | SFC Tank Level Bore Control Priority Setpoint 5 |  | % | ###EU | 0 | 100 | 0 | 100
|  | Analog |  |  | N_SFC_SFCLT01_STP_SP1 |  |  | INT | %MW5982 | SFC Tank Level Bore Control Stop Setpoint |  | % | ###EU | 0 | 100 | 0 | 100
|  | Analog |  |  | N_SFC_SFCLT01_STT_SP |  |  | INT | %MW5983 | SFC Tank Level Pump Control Start Setpoint |  | % | ###EU | 0 | 100 | 0 | 100
|  | Analog |  |  | N_SFC_SFCLT01_STP_SP |  |  | INT | %MW5984 | SFC Tank Level Pump Control Stop Setpoint |  | % | ###EU | 0 | 100 | 0 | 100
|  | Analog |  |  | N_SFC_SFCPUMPSREQ_SP |  |  | INT | %MW5985 | SFC Number of Pumps required to Run Setpoint |  |  |  | 0 | 32766 | 0 | 32766
|  | Analog |  |  | N_SFC_SFCP1_CNT_SP |  |  | INT | %MW5986 | P1 Counter Setpoint
|  | Analog |  |  | N_SFC_SFCP2_CNT_SP |  |  | INT | %MW5987 | P2 Counter Setpoint
|  | Analog |  |  | N_SFC_SFCP3_CNT_SP |  |  | INT | %MW5988 | P3 Counter Setpoint
|  | Analog |  |  | N_SFC_SFCP4_CNT_SP |  |  | INT | %MW5989 | P4 Counter Setpoint
|  | Analog |  |  | N_SFC_SFCP5_CNT_SP |  |  | INT | %MW5990 | P5 Counter Setpoint
|  | Analog |  |  | N_SFC_SFCFT01_YLDCD |  |  | INT | %MW10300 | SFC Tank Calculated In Flow Yield Current Day |  | m³ | #####EU | 0 | 32000 | 0 | 32000
|  | Analog |  |  | N_SFC_SFCFT01_YLDPD |  |  | INT | %MW10301 | SFC Tank Calculated In Flow Yield Previous Day |  | m³ | #####EU | 0 | 32000 | 0 | 32000
|  | Totalisers |  |  | N_SFC_SFCFT01_TOT.CurrDay |  |  | INT | %MW10260 | Current Day's Value |  | m³ | #####EU | 0 | 32767
|  | Totalisers |  |  | N_SFC_SFCFT01_TOT.PrevDay |  |  | INT | %MW10261 | Previous Day's Value |  | m³ | #####EU | 0 | 32767
|  | Totalisers |  |  | N_SFC_SFCFT01_TOT.CurrMonth |  |  | LONG | %MW10262 | Current Month's Value |  | m³ | #########EU | 0 | 1000000000
|  | Totalisers |  |  | N_SFC_SFCFT01_TOT.PrevMonth |  |  | LONG | %MW10264 | Previous Month's Value |  | m³ | #########EU | 0 | 1000000000
|  | Totalisers |  |  | N_SFC_SFCFT01_TOT.CurrYear |  |  | LONG | %MW10266 | Current Year's Value |  | m³ | #########EU | 0 | 1000000000
|  | Totalisers |  |  | N_SFC_SFCFT01_TOT.PrevYear |  |  | LONG | %MW10268 | Previous Month's Value |  | m³ | #########EU | 0 | 1000000000
[5 empty] | C_SFC_SFCBP01_PRIO_SP |  | CICODESVR | INT | LabelRetValue | BP01 Set Priority Command
[5 empty] | C_SFC_SFCBP02_PRIO_SP |  | CICODESVR | INT | LabelRetValue | BP02 Set Priority Command
[5 empty] | C_SFC_SFCBP03_PRIO_SP |  | CICODESVR | INT | LabelRetValue | BP03 Set Priority Command
[5 empty] | C_SFC_SFCBP04_PRIO_SP |  | CICODESVR | INT | LabelRetValue | BP04 Set Priority Command
[5 empty] | C_SFC_SFCBP05_PRIO_SP |  | CICODESVR | INT | LabelRetValue | BP05 Set Priority Command
[5 empty] | C_SFC_SFCBP06_PRIO_SP |  | CICODESVR | INT | LabelRetValue | BP06 Set Priority Command
[5 empty] | C_SFC_SFCBP07_PRIO_SP |  | CICODESVR | INT | LabelRetValue | BP07 Set Priority Command
[5 empty] | C_SFC_SFCBP08_PRIO_SP |  | CICODESVR | INT | LabelRetValue | BP08 Set Priority Command
[5 empty] | C_SFC_SFCBP09_PRIO_SP |  | CICODESVR | INT | LabelRetValue | BP09 Set Priority Command
[5 empty] | C_SFC_SFCBP10_PRIO_SP |  | CICODESVR | INT | LabelRetValue | BP10 Set Priority Command
[5 empty] | C_SFC_SFCBP11_PRIO_SP |  | CICODESVR | INT | LabelRetValue | BP11 Set Priority Command
[5 empty] | C_SFC_SFCBP12_PRIO_SP |  | CICODESVR | INT | LabelRetValue | BP12 Set Priority Command
[5 empty] | C_SFC_SFCBP13_PRIO_SP |  | CICODESVR | INT | LabelRetValue | BP13 Set Priority Command
[5 empty] | C_SFC_SFC_PT01_LO_SP |  | CICODESVR | INT | LabelRetValue | Pressure Low Setpoint Cmd
[5 empty] | C_SFC_SFC_LT01_HH_SP |  | CICODESVR | INT | LabelRetValue | Level High Setpoint Cmd
[5 empty] | C_SFC_SFC_LT01_LL_SP |  | CICODESVR | INT | LabelRetValue | Level Low Setpoint Cmd
[5 empty] | C_SFC_SFC_CLDWN_SP |  | CICODESVR | INT | LabelRetValue | Cooldown setpoint cmd
[5 empty] | C_SFC_SFC_LT01_STT_SP1 |  | CICODESVR | INT | LabelRetValue
[5 empty] | C_SFC_SFC_LT01_STT_SP2 |  | CICODESVR | INT | LabelRetValue
[5 empty] | C_SFC_SFC_LT01_STT_SP3 |  | CICODESVR | INT | LabelRetValue
[5 empty] | C_SFC_SFC_LT01_STT_SP4 |  | CICODESVR | INT | LabelRetValue
[5 empty] | C_SFC_SFC_LT01_STT_SP5 |  | CICODESVR | INT | LabelRetValue
[5 empty] | C_SFC_SFC_LT01_STP_SP1 |  | CICODESVR | INT | LabelRetValue | tank pumps stop setpoint cmd
[5 empty] | C_SFC_SFC_LT01_STT_SP |  | CICODESVR | INT | LabelRetValue | tank pumps start setpoint cmd
[5 empty] | C_SFC_SFC_LT01_STP_SP |  | CICODESVR | INT | LabelRetValue | tank pumps stop setpoint cmd
[5 empty] | C_SFC_SFC_LT02_SP |  | CICODESVR | INT | LabelRetValue | pressure tank level stop setpoint
[5 empty] | C_SFC_SFC_PT02_SP |  | CICODESVR | INT | LabelRetValue | pressure tank setpoint cmd
[5 empty] | C_SFC_SFC_ALMACK |  | CICODESVR | INT | LabelRetValue | reset cmd
[5 empty] | C_SFC_SFC_PRESS_RST |  | CICODESVR | INT | LabelRetValue | pressure reset cmd
[5 empty] | C_SFC_SFC_SUC_RST |  | CICODESVR | INT | LabelRetValue | suction pressure reset cmd
[5 empty] | C_SFC_SFC_PRIORITY_EN |  | CICODESVR | INT | LabelRetValue | priority enable cmd
[5 empty] | C_SFC_SFC_AUTDUTY |  | CICODESVR | INT | LabelRetValue | auto duty cmd
[5 empty] | C_SFC_SFC_PMPSSTOP |  | CICODESVR | INT | LabelRetValue | pumps stop cmd
[5 empty] | C_SFC_SFCP1_CNT_SP |  | CICODESVR | INT | LabelRetValue | P1 Counter SetPoint Command
[5 empty] | C_SFC_SFCP2_CNT_SP |  | CICODESVR | INT | LabelRetValue | P2 Counter SetPoint Command
[5 empty] | C_SFC_SFCP3_CNT_SP |  | CICODESVR | INT | LabelRetValue | P3 Counter SetPoint Command
[5 empty] | C_SFC_SFCP4_CNT_SP |  | CICODESVR | INT | LabelRetValue | P4 Counter SetPoint Command
[5 empty] | C_SFC_SFCP5_CNT_SP |  | CICODESVR | INT | LabelRetValue | P5 Counter SetPoint Command
[5 empty] | C_SFC_SFCSFB_CTRL_SEL |  | CICODESVR | INT | LabelRetValue | Pump Control Selection: SFB Tank or Town Tank
[5 empty] | C_SFC_SFCTTNK_CTRL_SEL |  | CICODESVR | INT | LabelRetValue | Town Tank Selected to Control SFC Pumps
[5 empty] | C_SFC_SFCPUMPSREQ_SP |  | CICODESVR | INT | LabelRetValue | Pumps Required for SP
|  | Alarm |  | TP_CRIT_CAT | A_SFC_SFC24VDC_FLT |  |  | DIGITAL | %M10785 | SFC 24VDC Failed
|  | Alarm |  | TP_CRIT_CAT | A_SFC_SFC110V_FLT |  |  | DIGITAL | %M10786 | SFC 110V MCC
|  | Alarm |  | TP_CRIT_CAT | A_SFC_SFCLT01_BPV |  |  | DIGITAL | %M10791 | SFC Tank Level Transmitter Bad Process Variable
|  | Alarm |  | TP_CRIT_CAT | A_SFC_SFCLT01_HH |  |  | DIGITAL | %M10792 | SFC Tank Level High High
|  | Alarm |  | TP_CRIT_CAT | A_SFC_SFCLT01_LL |  |  | DIGITAL | %M10793 | SFC Tank Level Low Low
|  | Alarm |  | TP_CRIT_CAT | A_SFC_SFCLT02_BPV |  |  | DIGITAL | %M10794 | SFC Surge Vessel Level Bad Process Variable
|  | Alarm |  | TP_CRIT_CAT | A_SFC_SFCLT02_HH |  |  | DIGITAL | %M10795 | SFC Surge Vessel Level High High
|  | Alarm |  | TP_CRIT_CAT | A_SFC_SFCLT02_LL |  |  | DIGITAL | %M10796 | SFC Surge Vessel Level Low Low
|  | Alarm |  | TP_CRIT_CAT | A_SFC_SFCPT01_BPV |  |  | DIGITAL | %M10797 | SFC Line Pressure Transmitter Bad Process Variable
|  | Alarm |  | TP_CRIT_CAT | A_SFC_SFCPT01_LO |  |  | DIGITAL | %M10798 | SFC Line Pressure Low
|  | Alarm |  | TP_CRIT_CAT | A_SFC_SFCPT02_BPV |  |  | DIGITAL | %M10799 | SFC Surge Vessel Pressure Transmitter Bad Process Variable
|  | Alarm |  | TP_CRIT_CAT | A_SFC_SFCPT02_HH |  |  | DIGITAL | %M10800 | SFC Surge Vessel Pressure High High
|  | Alarm |  | TP_CRIT_CAT | A_SFC_SFCPT02_LL |  |  | DIGITAL | %M10801 | SFC Surge Vessel Pressure Low Low
|  | Alarm |  | TP_CRIT_CAT | A_SFC_SFCSUC_PRESS |  |  | DIGITAL | %M10802 | SFC Suction Pressure Low Low
|  | Alarm |  | TP_CRIT_CAT | A_SFC_SFCTKLS_DISC |  |  | DIGITAL | %M10803 | SFC level sw discrepancy
|  | Status |  |  | S_SFC_SFCPRIORITYRUN |  |  | DIGITAL | %M2282 | SFC Bore Pumps Priority Control Running Status
|  | Status |  |  | S_SFC_SFCTTNKCTRL_SEL |  |  | DIGITAL | %M2283 | SFC Tank Control Selection
|  | Status |  |  | S_SFC_SFCSFBCTRL_SEL |  |  | DIGITAL | %M2284 | SFC/SFB Control
|  | Status |  |  | S_SFC_SFCPx_EN |  |  | DIGITAL | %M2285 | SFC Pump Enabled
|  | Status |  |  | S_SFC_SFCAUTDUTY |  |  | DIGITAL | %M2286 | SFC Auto Duty Selected

## SFB
Equipment | Item Name | Tag Type | Set Trend | Category | Tag Name | Cluster Name | I/O Device | Data Type | Address | Comment | Deadband | Eng Units | Format | Raw Zero Scale | Raw Full Scale | Eng Zero Scale | Eng Full Scale | Custom 1 | Custom 2 | Custom 3 | Custom 4 | Custom 5 | Custom 6 | Custom 7 | Custom 8 | Historize | Project | EDITCODE | LINKED | OID | REF1 | REF2 | CUSTOM | TAGGENLINK
[5 empty] | Alarm |  |  |  | 11051
[5 empty] | Analog |  |  |  | 2090
[5 empty] | Status |  |  |  | 2600
[5 empty] | Totalisers |  |  |  | 11100
SFC_SFB |  | Alarm |  | TP_CRIT_CAT | A_SFC_SFB_24VDC_FLT |  |  | DIGITAL | %M11051 | SFB 24VDC Failed Alarm
|  | Alarm |  | TP_CRIT_CAT | A_SFC_SFBSUC_PRESS |  |  | DIGITAL | %M11052 | SFB Suction Pressure Low Alarm
|  | Alarm |  | TP_CRIT_CAT | A_SFC_SFBPT01_LO |  |  | DIGITAL | %M11053 | SFB PRESSURE LOW ALARM
|  | Alarm |  | TP_CRIT_CAT | A_SFC_SFBLT01_HH |  |  | DIGITAL | %M11054 | SFB TANK LEVEL HIGH ALARM
|  | Alarm |  | TP_CRIT_CAT | A_SFC_SFBLT01_LL |  |  | DIGITAL | %M11055 | SFB TANK LEVEL LOW ALARM
|  | Alarm |  | TP_CRIT_CAT | A_SFC_SFB_FLOW_LO |  |  | DIGITAL | %M11056 | PS DISCHARGE FLOW LOW ALARM
|  | Alarm |  | TP_CRIT_CAT | A_SFC_SFBTKLS_DISC |  |  | DIGITAL | %M11057 | SFB LEVEL SW DISCREP ALARM
|  | Alarm |  | TP_CRIT_CAT | A_SFC_SFBCHL_RES_LL |  |  | DIGITAL | %M11058 | SFB Chlorine Residual Low Alarm
|  | Status |  |  | S_SFC_SFB_110V_OK |  |  | DIGITAL | %M2600 | PS Panel 110V OK Status
|  | Status |  |  | S_SFC_SFB_SUW |  |  | DIGITAL | %M2601 | SFB Pump Startup Warning Siren On
|  | Status |  |  | S_SFC_SFBCHL_RES_BYP |  |  | DIGITAL | %M2606 | Chlorine Residue Bypass
|  | Status |  |  | S_SFC_SFBAUTDUTY |  |  | DIGITAL | %M2608 | SFB Auto Duty Selected
|  | Analog |  |  | N_SFC_SFB_FT01_YLDCD |  |  | INT | %MW2090 | SFB Tank Calculated In Flow Yield Current Day
|  | Analog |  |  | N_SFC_SFB_FT01_YLDPD |  |  | INT | %MW2091 | SFB Tank Calculated In Flow Yield Previous Day
|  | Analog |  |  | N_SFC_SFB_FT01_YLD |  |  | LONG | %MW2092 | Total Accum Flow
|  | Analog |  |  | N_SFC_SFBP1_HRSCD |  |  | INT | %MW2098 | P1 Current Day Accumulated Run Hours |  | Hrs | #.##EU | 0 | 2400 | 0 | 24
|  | Analog |  |  | N_SFC_SFBP1_HRSPD |  |  | INT | %MW2099 | P1 Previous Day Accumulated Run Hours |  | Hrs | #.##EU | 0 | 2400 | 0 | 24
|  | Analog |  |  | N_SFC_SFBP1_HRS |  |  | LONG | %MW2100 | P1 Total Accum Run Hours |  | Hrs | ########EU | 0 | 240000000 | 0 | 2400000
|  | Analog |  |  | N_SFC_SFBP1_KWHCD |  |  | INT | %MW2102 | P2 Current Day Accumulated Run Hours |  | Hrs | #.##EU | 0 | 2400 | 0 | 24
|  | Analog |  |  | N_SFC_SFBP1_KWHPD |  |  | INT | %MW2103 | P2 Previous Day Accumulated Run Hours |  | Hrs | #.##EU | 0 | 2400 | 0 | 24
|  | Analog |  |  | N_SFC_SFBP1_KWH |  |  | LONG | %MW2104 | P2 Total Accum Run Hours |  | Hrs | ########EU | 0 | 240000000 | 0 | 2400000
|  | Analog |  |  | N_SFC_SFBP2_HRSCD |  |  | INT | %MW2106 | P3 Current Day Accumulated Run Hours |  | Hrs | #.##EU | 0 | 2400 | 0 | 24
|  | Analog |  |  | N_SFC_SFBP2_HRSPD |  |  | INT | %MW2107 | P3 Previous Day Accumulated Run Hours |  | Hrs | #.##EU | 0 | 2400 | 0 | 24
|  | Analog |  |  | N_SFC_SFBP2_HRS |  |  | LONG | %MW2108 | P3 Total Accum Run Hours |  | Hrs | ########EU | 0 | 240000000 | 0 | 2400000
|  | Analog |  |  | N_SFC_SFBP2_KWHCD |  |  | INT | %MW2110 | P4 Current Day Accumulated Run Hours |  | Hrs | #.##EU | 0 | 2400 | 0 | 24
|  | Analog |  |  | N_SFC_SFBP2_KWHPD |  |  | INT | %MW2111 | P4 Previous Day Accumulated Run Hours |  | Hrs | #.##EU | 0 | 2400 | 0 | 24
|  | Analog |  |  | N_SFC_SFBP2_KWH |  |  | LONG | %MW2112 | P4 Total Accum Run Hours |  | Hrs | ########EU | 0 | 240000000 | 0 | 2400000
|  | Analog |  |  | N_SFC_SFBP3_HRSCD |  |  | INT | %MW2114 | P5 Current Day Accumulated Run Hours |  | Hrs | #.##EU | 0 | 2400 | 0 | 24
|  | Analog |  |  | N_SFC_SFBP3_HRSPD |  |  | INT | %MW2115 | P5 Previous Day Accumulated Run Hours |  | Hrs | #.##EU | 0 | 2400 | 0 | 24
|  | Analog |  |  | N_SFC_SFBP3_HRS |  |  | LONG | %MW2116 | P5 Total Accum Run Hours |  | Hrs | ########EU | 0 | 240000000 | 0 | 2400000
|  | Analog |  |  | N_SFC_SFBP3_KWHCD |  |  | INT | %MW2118 | P1 Current Day Accumulated KWH |  | kWh | ####.#EU | 0 | 10000 | 0 | 1000
|  | Analog |  |  | N_SFC_SFBP3_KWHPD |  |  | INT | %MW2119 | P1 Previous Day Accumulated KWH |  | kWh | ####.#EU | 0 | 10000 | 0 | 1000
|  | Analog |  |  | N_SFC_SFBP3_KWH |  |  | LONG | %MW2120 | P1 Accumulated KWH |  | kWh
|  | Analog |  |  | N_SFC_SFBP4_HRSCD |  |  | INT | %MW2122 | P2 Current Day Accumulated KWH |  | kWh | ####.#EU | 0 | 10000 | 0 | 1000
|  | Analog |  |  | N_SFC_SFBP4_HRSPD |  |  | INT | %MW2123 | P2 Previous Day Accumulated KWH |  | kWh | ####.#EU | 0 | 10000 | 0 | 1000
|  | Analog |  |  | N_SFC_SFBP4_HRS |  |  | LONG | %MW2124 | P2 Accumulated KWH |  | kWh
|  | Analog |  |  | N_SFC_SFBP4_KWHCD |  |  | INT | %MW2126 | P3 Current Day Accumulated KWH |  | kWh | ####.#EU | 0 | 10000 | 0 | 1000
|  | Analog |  |  | N_SFC_SFBP4_KWHPD |  |  | INT | %MW2127 | P3 Previous Day Accumulated KWH |  | kWh | ####.#EU | 0 | 10000 | 0 | 1000
|  | Analog |  |  | N_SFC_SFBP4_KWH |  |  | LONG | %MW2128 | P3 Accumulated KWH |  | kWh
|  | Analog |  |  | N_SFC_SFBP5_HRSCD |  |  | INT | %MW2130 | P4 Current Day Accumulated KWH |  | kWh | ####.#EU | 0 | 10000 | 0 | 1000
|  | Analog |  |  | N_SFC_SFBP5_HRSPD |  |  | INT | %MW2131 | P4 Previous Day Accumulated KWH |  | kWh | ####.#EU | 0 | 10000 | 0 | 1000
|  | Analog |  |  | N_SFC_SFBP5_HRS |  |  | LONG | %MW2132 | P4 Accumulated KWH |  | kWh
|  | Analog |  |  | N_SFC_SFBP5_KWHCD |  |  | INT | %MW2134 | P5 Current Day Accumulated KWH |  | kWh | ####.#EU | 0 | 10000 | 0 | 1000
|  | Analog |  |  | N_SFC_SFBP5_KWHPD |  |  | INT | %MW2135 | P5 Previous Day Accumulated KWH |  | kWh | ####.#EU | 0 | 10000 | 0 | 1000
|  | Analog |  |  | N_SFC_SFBP5_KWH |  |  | LONG | %MW2136 | P5 Accumulated KWH |  | kWh
|  | Totalisers |  |  | N_SFC_SFBFT01_TOT.CurrDay |  |  | INT | %MW11100 | Current Day's Value |  | m³ | #####EU | 0 | 32767 | 0 | 32767
|  | Totalisers |  |  | N_SFC_SFBFT01_TOT.PrevDay |  |  | INT | %MW11101 | Previous Day's Value |  | m³ | #####EU | 0 | 32767 | 0 | 32767
|  | Totalisers |  |  | N_SFC_SFBFT01_TOT.CurrMonth |  |  | LONG | %MW11102 | Current Month's Value |  | m³ | #########EU | 0 | 1000000000 | 0 | 1000000000
|  | Totalisers |  |  | N_SFC_SFBFT01_TOT.PrevMonth |  |  | LONG | %MW11104 | Previous Month's Value |  | m³ | #########EU | 0 | 1000000000 | 0 | 1000000000
|  | Totalisers |  |  | N_SFC_SFBFT01_TOT.CurrYear |  |  | LONG | %MW11106 | Current Year's Value |  | m³ | #########EU | 0 | 1000000000 | 0 | 1000000000
|  | Totalisers |  |  | N_SFC_SFBFT01_TOT.PrevYear |  |  | LONG | %MW11108 | Previous Month's Value |  | m³ | #########EU | 0 | 1000000000 | 0 | 1000000000
|  | Analog | TRUE |  | N_SFC_SFBLT01_PV |  |  | INT | %MW2301 | booster tank level (%) |  | % | ###EU | 0 | 100 | 0 | 100
|  | Analog | TRUE |  | N_SFC_SFBCHL_Res1 |  |  | INT | %MW2302 | chlorine residual level |  | ppm | #.##EU | 0 | 2 | 0 | 2
|  | Analog | TRUE |  | N_SFC_SFBP1TT03_PV |  |  | INT | %MW2303 | SFC Pump P1 Pump DE Bearing Temperature |  | °C | #### EU | 0 | 32766 | 0 | 32766
|  | Analog | TRUE |  | N_SFC_SFBP1TT04_PV |  |  | INT | %MW2304 | SFC Pump P1 Pump NDE Bearing Temperature |  | °C | #### EU | 0 | 32766 | 0 | 32766
|  | Analog | TRUE |  | N_SFC_SFBM1TT01_PV |  |  | INT | %MW2305 | SFC Pump P1 Motor DE Bearing Temperature |  | °C | #### EU | 0 | 32766 | 0 | 32766
|  | Analog | TRUE |  | N_SFC_SFBM1TT02_PV |  |  | INT | %MW2306 | SFC Pump P1 Motor NDE Bearing Temperature |  | °C | #### EU | 0 | 32766 | 0 | 32766
|  | Analog | TRUE |  | N_SFC_SFBP2TT03_PV |  |  | INT | %MW2307 | SFC Pump P2 Pump DE Bearing Temperature |  | °C | #### EU | 0 | 32766 | 0 | 32766
|  | Analog | TRUE |  | N_SFC_SFBP2TT04_PV |  |  | INT | %MW2308 | SFC Pump P2 Pump NDE Bearing Temperature |  | °C | #### EU | 0 | 32766 | 0 | 32766
|  | Analog | TRUE |  | N_SFC_SFBM2TT01_PV |  |  | INT | %MW2309 | SFC Pump P2 Motor DE Bearing Temperature |  | °C | #### EU | 0 | 32766 | 0 | 32766
|  | Analog | TRUE |  | N_SFC_SFBM2TT02_PV |  |  | INT | %MW2310 | SFC Pump P2 Motor NDE Bearing Temperature |  | °C | #### EU | 0 | 32766 | 0 | 32766
|  | Analog | TRUE |  | N_SFC_SFBP3TT03_PV |  |  | INT | %MW2311 | SFC Pump P3 Pump DE Bearing Temperature |  | °C | #### EU | 0 | 32766 | 0 | 32766
|  | Analog | TRUE |  | N_SFC_SFBP3TT04_PV |  |  | INT | %MW2312 | SFC Pump P3 Pump NDE Bearing Temperature |  | °C | #### EU | 0 | 32766 | 0 | 32766
|  | Analog | TRUE |  | N_SFC_SFBM3TT01_PV |  |  | INT | %MW2313 | SFC Pump P3 Motor DE Bearing Temperature |  | °C | #### EU | 0 | 32766 | 0 | 32766
|  | Analog | TRUE |  | N_SFC_SFBM3TT02_PV |  |  | INT | %MW2314 | SFC Pump P3 Motor NDE Bearing Temperature |  | °C | #### EU | 0 | 32766 | 0 | 32766
|  | Analog | TRUE |  | N_SFC_SFBP4TT03_PV |  |  | INT | %MW2315 | SFC Pump P4 Pump DE Bearing Temperature |  | °C | #### EU | 0 | 32766 | 0 | 32766
|  | Analog | TRUE |  | N_SFC_SFBP4TT04_PV |  |  | INT | %MW2316 | SFC Pump P4 Pump NDE Bearing Temperature |  | °C | #### EU | 0 | 32766 | 0 | 32766
|  | Analog | TRUE |  | N_SFC_SFBM4TT01_PV |  |  | INT | %MW2317 | SFC Pump P4 Motor DE Bearing Temperature |  | °C | #### EU | 0 | 32766 | 0 | 32766
|  | Analog | TRUE |  | N_SFC_SFBM4TT02_PV |  |  | INT | %MW2318 | SFC Pump P4 Motor NDE Bearing Temperature |  | °C | #### EU | 0 | 32766 | 0 | 32766
|  | Analog | TRUE |  | N_SFC_SFBP5TT03_PV |  |  | INT | %MW2319 | SFC Pump P5 Pump DE Bearing Temperature |  | °C | #### EU | 0 | 32766 | 0 | 32766
|  | Analog | TRUE |  | N_SFC_SFBP5TT04_PV |  |  | INT | %MW2320 | SFC Pump P5 Pump NDE Bearing Temperature |  | °C | #### EU | 0 | 32766 | 0 | 32766
|  | Analog | TRUE |  | N_SFC_SFBM5TT01_PV |  |  | INT | %MW2321 | SFC Pump P5 Motor DE Bearing Temperature |  | °C | #### EU | 0 | 32766 | 0 | 32766
|  | Analog | TRUE |  | N_SFC_SFBM5TT02_PV |  |  | INT | %MW2322 | SFC Pump P5 Motor NDE Bearing Temperature |  | °C | #### EU | 0 | 32766 | 0 | 32766
|  | Analog | TRUE |  | N_SFC_SFBPT01_PV |  |  | INT | %MW2323 | SFB Line Pressure (kPa) |  | kPa | ####EU | 0 | 5500 | 0 | 5500
|  | Analog |  |  | N_SFC_SFBLT01_STT_SP |  |  | INT | %MW2601 | SFB Tank Start Level Pump Control Setpoint |  | % | ###EU | 0 | 100 | 0 | 100
|  | Analog |  |  | N_SFC_SFBLT01_STP_SP |  |  | INT | %MW2602 | SFB Tank Stop Level Pump Control Setpoint |  | % | ###EU | 0 | 100 | 0 | 100
|  | Analog |  |  | N_SFC_SFBPUMPSREQ_SP |  |  | INT | %MW2603 | SFB Number of Pumps required to Run Setpoint |  |  |  | 0 | 32766 | 0 | 32766
|  | Analog |  |  | N_SFC_SFBP1_CNT_SP |  |  | INT | %MW2604 | SFB Pump P01 Counter Setpoint
|  | Analog |  |  | N_SFC_SFBP2_CNT_SP |  |  | INT | %MW2605 | SFB Pump P02 Counter Setpoint
|  | Analog |  |  | N_SFC_SFBP3_CNT_SP |  |  | INT | %MW2606 | SFB Pump P03 Counter Setpoint
|  | Analog |  |  | N_SFC_SFBP4_CNT_SP |  |  | INT | %MW2607 | SFB Pump P04 Counter Setpoint
|  | Analog |  |  | N_SFC_SFBP5_CNT_SP |  |  | INT | %MW2608 | SFB Pump P05 Counter Setpoint
|  | Analog |  |  | N_SFC_SFB_SFCLT01_STT_SP |  |  | INT | %MW2609 | Collector tank level start setpoint
|  | Analog |  |  | N_SFC_SFB_SFCLT01_STP_SP |  |  | INT | %MW2610 | Collector tank level stop setpoint
[5 empty] | C_SFC_SFBPUMPSREQ_SP |  | CICODESVR | INT | LabelRetValue | Pumps Required for SP
[5 empty] | C_SFC_SFB_LT01_STT_SP |  | CICODESVR | INT | LabelRetValue | tank pumps start setpoint cmd
[5 empty] | C_SFC_SFB_LT01_STP_SP |  | CICODESVR | INT | LabelRetValue | tank pumps stop setpoint cmd
[5 empty] | C_SFC_SFBP1_CNT_SP |  | CICODESVR | INT | LabelRetValue | P1 Counter SetPoint Command
[5 empty] | C_SFC_SFBP2_CNT_SP |  | CICODESVR | INT | LabelRetValue | P2 Counter SetPoint Command
[5 empty] | C_SFC_SFBP3_CNT_SP |  | CICODESVR | INT | LabelRetValue | P3 Counter SetPoint Command
[5 empty] | C_SFC_SFBP4_CNT_SP |  | CICODESVR | INT | LabelRetValue | P4 Counter SetPoint Command
[5 empty] | C_SFC_SFBP5_CNT_SP |  | CICODESVR | INT | LabelRetValue | P5 Counter SetPoint Command
[5 empty] | C_SFC_SFB_ALMACK |  | CICODESVR | INT | LabelRetValue | reset cmd
[5 empty] | C_SFC_SFB_PRESS_RST |  | CICODESVR | INT | LabelRetValue | pressure reset cmd
[5 empty] | C_SFC_SFB_AUTDUTY |  | CICODESVR | INT | LabelRetValue | auto duty cmd
[5 empty] | C_SFC_SFB_PMPSSTOP |  | CICODESVR | INT | LabelRetValue | pumps stop cmd
[5 empty] | C_SFC_SFB_SFCLT01_STT_SP |  | CICODESVR | INT | LabelRetValue | Collector tank level start setpoint Command
[5 empty] | C_SFC_SFB_SFCLT01_STP_SP |  | CICODESVR | INT | LabelRetValue | Collector tank level stop setpoint Command
|  | Analog | TRUE |  | N_SFC_SFBFT01_PV |  |  | INT | %MW2324 | Flow rate? |  | m³/Hr | #####EU | 0 | 32000 | 0 | 32000
|  | Analog |  |  | N_SFC_SFBP1_STT_CNT |  |  | LONG | %MW2612 | P1 Auto Duty Rotation Start Count |  |  |  | 0 | 32766 | 0 | 32766
|  | Analog |  |  | N_SFC_SFBP2_STT_CNT |  |  | LONG | %MW2614 | P2 Auto Duty Rotation Start Count |  |  |  | 0 | 32766 | 0 | 32766
|  | Analog |  |  | N_SFC_SFBP3_STT_CNT |  |  | LONG | %MW2616 | P3 Auto Duty Rotation Start Count |  |  |  | 0 | 32766 | 0 | 32766
|  | Analog |  |  | N_SFC_SFBP4_STT_CNT |  |  | LONG | %MW2618 | P4 Auto Duty Rotation Start Count |  |  |  | 0 | 32766 | 0 | 32766
|  | Analog |  |  | N_SFC_SFBP5_STT_CNT |  |  | LONG | %MW2620 | P5 Auto Duty Rotation Start Count |  |  |  | 0 | 32766 | 0 | 32766

## Chlorinator
Equipment | Item Name | Tag Type | Set Trend | Category | Tag Name | Cluster Name | I/O Device | Data Type | Address | Comment | Deadband | Eng Units | Format | Raw Zero Scale | Raw Full Scale | Eng Zero Scale | Eng Full Scale | Custom 1 | Custom 2 | Custom 3 | Custom 4 | Custom 5 | Custom 6 | Custom 7 | Custom 8 | Historize | Project | EDITCODE | LINKED | OID | REF1 | REF2 | CUSTOM | TAGGENLINK
[5 empty] | Status |  |  |  | 0
[5 empty] | Analog |  |  |  | 5804
[5 empty] | Totalisers |  |  |  | 0
[5 empty] | Alarm |  |  |  | 10782
SFC_CL2 |  | Analog | TRUE |  | N_SFC_CL2_PV |  |  | REAL | %MW5804 | SFC Chlorine (mg/l) |  | mg/l | #.##EU | 0 | 2 | 0 | 2
|  | Analog | TRUE |  | N_SFC_CL2WGHT1_PV |  |  | INT | %MW5806 | SFC Chlorine Load Cell Weight 1 (kg) |  | kg | ####EU | 0 | 1000 | 0 | 1000
|  | Analog | TRUE |  | N_SFC_CL2WGHT2_PV |  |  | INT | %MW5807 | SFC Chlorine Load Cell Weight 2 (kg) |  | kg | ####EU | 0 | 1000 | 0 | 1000
|  | Alarm |  | TP_CRIT_CAT | A_SFC_CL2_BPV |  |  | DIGITAL | %M10782 | SFC Chlorine Transmitter Bad Process Variable
|  | Alarm |  | TP_CRIT_CAT | A_SFC_CL2WGHT1_BPV |  |  | DIGITAL | %M10783 | SFC Chlorine Load Cell Weight 1 Bad Process Variable
|  | Alarm |  | TP_CRIT_CAT | A_SFC_CL2WGHT2_BPV |  |  | DIGITAL | %M10784 | SFC Chlorine Load Cell Weight 2 Bad Process Variable
|  | Alarm |  | TP_CRIT_CAT | A_SFC_CL2_FLT |  |  | DIGITAL | %M10787 | SFC Chlorine General
|  | Alarm |  | TP_CRIT_CAT | A_SFC_CL2_LEAK_HI |  |  | DIGITAL | %M10788 | SFC Chlorine Leak High
|  | Alarm |  | TP_CRIT_CAT | A_SFC_CL2_LEAK_LO |  |  | DIGITAL | %M10789 | SFC Chlorine Leak Low
|  | Alarm |  | TP_CRIT_CAT | A_SFC_CL2_SYS_POWER |  |  | DIGITAL | %M10790 | SFC Chlorine Power Fail

## Compressor
Equipment | Item Name | Tag Type | Set Trend | Category | Tag Name | Cluster Name | I/O Device | Data Type | Address | Comment | Deadband | Eng Units | Format | Raw Zero Scale | Raw Full Scale | Eng Zero Scale | Eng Full Scale | Custom 1 | Custom 2 | Custom 3 | Custom 4 | Custom 5 | Custom 6 | Custom 7 | Custom 8 | Historize | Project | EDITCODE | LINKED | OID | REF1 | REF2 | CUSTOM | TAGGENLINK
[5 empty] | Alarm |  |  |  | 10750
[5 empty] | Analog |  |  |  | 5651
[5 empty] | Totalisers |  |  |  | 10690
[5 empty] | Status |  |  |  | 2250
SFC_CP01 |  | Alarm |  | TP_CRIT_CAT | A_SFC_CP01_FLT |  |  | DIGITAL | %M10750 | Fault
|  | Alarm |  | TP_CRIT_CAT | A_SFC_CP01_CA1_FLT |  |  | DIGITAL | %M10751 | Contactor Fault
|  | Alarm |  | TP_CRIT_CAT | A_SFC_CP01_RUNFLT |  |  | DIGITAL | %M10752 | Running for too long Fault
|  | Status |  |  | S_SFC_CP01_AUTO |  |  | DIGITAL | %M2250 | Auto Status
|  | Status |  |  | S_SFC_CP01_LOCAL |  |  | DIGITAL | %M2251 | Local Status
|  | Status |  |  | S_SFC_CP01_MAN |  |  | DIGITAL | %M2252 | Manual Status
|  | Status |  |  | S_SFC_CP01_OFF |  |  | DIGITAL | %M2253 | Off Status
|  | Status |  |  | S_SFC_CP01_OTM |  |  | DIGITAL | %M2254 | Maintenance Status
|  | Status |  |  | S_SFC_CP01_BIT1 |  |  | DIGITAL | %M2255 | Status Bit 1
|  | Status |  |  | S_SFC_CP01_BIT2 |  |  | DIGITAL | %M2256 | Status Bit 2
|  | Status |  |  | S_SFC_CP01_BIT3 |  |  | DIGITAL | %M2257 | Status Bit 3
|  | Status |  |  | S_SFC_CP01_BIT4 |  |  | DIGITAL | %M2258 | Status Bit 4
|  | Status |  |  | S_SFC_CP01_CLDWN |  |  | DIGITAL | %M2259 | Cooling Down Status
|  | Status |  |  | S_SFC_CP01_RDY |  |  | DIGITAL | %M2260 | Ready Status
|  | Status |  |  | S_SFC_CP01_RUNNG |  |  | DIGITAL | %M2261 | Running Status
|  | Status |  |  | S_SFC_CP01_PMPINH |  |  | DIGITAL | %M2262 | Pumps Inhibit Status
|  | Status |  |  | S_SFC_CP01_CA |  |  | DIGITAL | %M2266 | Contactor status
|  | Status |  |  | S_SFC_CP01_CILK |  |  | DIGITAL | %M2267 | Critical Interlock
|  | Status |  |  | S_SFC_CP01_SEQILK |  |  | DIGITAL | %M2268 | Sequence Interlock
|  | Status |  |  | S_SFC_CP01_NCILK |  |  | DIGITAL | %M2269 | Non Critical Interlock
|  | Analog |  |  | N_SFC_CP01_HRSCD |  |  | INT | %MW5651 | Current Day Accumulated Run Hours |  | Hrs | #.##EU | 0 | 2400 | 0 | 24
|  | Analog |  |  | N_SFC_CP01_HRSPD |  |  | INT | %MW5652 | Previous Day Accumulated Run Hours |  | Hrs | #.##EU | 0 | 2400 | 0 | 24
|  | Analog |  |  | N_SFC_CP01_HRS |  |  | LONG | %MW5654 | Total Accumulated Run Hours |  | Hrs | ########EU | 0 | 240000000 | 0 | 2400000
|  | Totalisers |  |  | N_SFC_CP01Hrs_TOT.CurrDay |  |  | INT | %MW10690 | Current Day's Value |  | Hrs | #.##EU | 0 | 2400 | 0 | 24
|  | Totalisers |  |  | N_SFC_CP01Hrs_TOT.PrevDay |  |  | INT | %MW10691 | Previous Day's Value |  | Hrs | #.##EU | 0 | 2400 | 0 | 24
|  | Totalisers |  |  | N_SFC_CP01Hrs_TOT.CurrMonth |  |  | LONG | %MW10692 | Current Month's Value |  | Hrs | #########EU | 0 | 240000000 | 0 | 2400000
|  | Totalisers |  |  | N_SFC_CP01Hrs_TOT.PrevMonth |  |  | LONG | %MW10694 | Previous Month's Value |  | Hrs | #########EU | 0 | 240000000 | 0 | 2400000
|  | Totalisers |  |  | N_SFC_CP01Hrs_TOT.CurrYear |  |  | LONG | %MW10696 | Current Years Value |  | Hrs | #########EU | 0 | 240000000 | 0 | 2400000
|  | Totalisers |  |  | N_SFC_CP01Hrs_TOT.PrevYear |  |  | LONG | %MW10698 | Previous Years Value |  | Hrs | #########EU | 0 | 240000000 | 0 | 2400000
[5 empty] | C_SFC_CP01_ALMACK |  | CICODESVR | INT | LabelRetValue | Alarm Ack Command
[5 empty] | C_SFC_CP01_AUTO |  | CICODESVR | INT | LabelRetValue | Auto Command
[5 empty] | C_SFC_CP01_LOCAL |  | CICODESVR | INT | LabelRetValue | Local Command
[5 empty] | C_SFC_CP01_MAN |  | CICODESVR | INT | LabelRetValue | Manual/Remote Command
[5 empty] | C_SFC_CP01_OFF |  | CICODESVR | INT | LabelRetValue | Off Command
[5 empty] | C_SFC_CP01_OTM |  | CICODESVR | INT | LabelRetValue | Out to Maint Command
[5 empty] | C_SFC_CP01_STP |  | CICODESVR | INT | LabelRetValue | Stop Command
[5 empty] | C_SFC_CP01_STT |  | CICODESVR | INT | LabelRetValue | Start Command
[5 empty] | C_SFC_CP01_STTR |  | CICODESVR | INT | LabelRetValue | Dump Command